## Key
Abbreviation | Quantity | Description
P_in | Input power | Three-phase power measured at transformer high side (primary terminals)
P_sec | Transformer secondary power | Three-phase power measured at transformer low side (secondary terminals)
P_out | Output power | Total output power (sum of load powers)
P_loss | System loss | Estimated system loss = P_in - P_out
P_lossTran | Transformer loss | Estimated transformer loss = P_in - P_sec
P_lossConv | Converter loss | Estimated converter loss = P_sec - P_out
V_load | Load voltage | DC or AC (RMS) voltage measured at a load's terminals (each load)
I_load | Load current | DC or AC (RMS) current measured at a load's terminals (each load)
R_load | Load resistance | Fixed load resistance measured during characterization test (each load)
P_load | Load power | Calculated load power (each load)
σ(x) | Standard deviation | Experimental estimate of standard deviation for quantity x, calculated unless x was measured directly
Calc: x | Calculated value | Calculated version of x, as a secondary check
Note on A1: Correcting heater outputs. (Setting output DC power to 0W) -Avpreet Singh Othee

## Scenarios 1-2
Scenarios 1-2: AC Balanced, Unbalanced | [96 empty] | Model Results |  |  |  |  | Estimates of Error (90% Confidence Interval)
Metadata | Load: Laptop Charger 3 |  |  |  | Load: Laptop Charger 4 |  |  |  | Load: Laptop Charger 5 |  |  |  | Load: LED 1 |  |  |  | Load: LED 2 |  |  |  | Load: LED 3 |  |  |  | Load: PS1 |  |  |  | Load: PS2 |  |  |  | Load: PS3 |  |  |  | Input | Trans. Secondary | Output |  | Loss |  |  |  |  | Load: Laptop Charger 3 |  |  |  |  | Load: Laptop Charger 4 |  |  |  |  | Load: Laptop Charger 5 |  |  |  |  | Load: LED 1 |  |  |  |  | Load: LED 2 |  |  |  |  | Load: LED 3 |  |  |  |  | Load: PS1 |  |  |  | Load: PS2 |  |  |  | Load: PS3 |  |  |  | Input | Trans. Secondary | Output |  | Loss |  |  |  |  | Power Values |  |  |  |  | Input Power: P_in |  |  |  | Transformer Secondary Power: P_sec |  |  |  | Transformer Loss: P_lossTran |  |  |  | Converter Loss: P_lossConv |  |  |  | System Loss: P_loss
Data Set | V_load [V] | I_load [A] | P_load [W] | Calc: P_load [W] | V_load [V] | I_load [A] | P_load [W] | Calc: P_load [W] | V_load [V] | I_load [A] | P_load [W] | Calc: P_load [W] | V_load [V] | I_load [A] | P_load [W] | Calc: P_load [W] | V_load [V] | I_load [A] | P_load [W] | Calc: P_load [W] | V_load [V] | I_load [A] | P_load [W] | Calc: P_load [W] | V_load [V] | R_load [Ω] | P_load [W] | Calc: P_load [W] | V_load [V] | R_load [Ω] | P_load [W] | Calc: P_load [W] | V_load [V] | R_load [Ω] | P_load [W] | Calc: P_load [W] | P_in [W] | P_sec [W] | P_out [W] | Calc: P_out [W] | P_lossTran [W] | P_lossConv [W] | Calc: P_lossConv [W] | P_loss [W] | Calc: P_loss [W] | σ(V_load) [V] | σ(I_load) [A] | COV(V_load,I_load) [(VA)²] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(I_load) [A] | COV(V_load,I_load) [(VA)²] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(I_load) [A] | COV(V_load,I_load) [(VA)²] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(I_load) [A] | COV(V_load,I_load) [(VA)²] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(I_load) [A] | COV(V_load,I_load) [(VA)²] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(I_load) [A] | COV(V_load,I_load) [(VA)²] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(R_load) [Ω] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(R_load) [Ω] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(R_load) [Ω] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(P_in) [W] | σ(P_sec) [W] | σ(P_out) [W] | Calc: σ(P_out) [W] | σ(P_lossTran) [W] | σ(P_lossConv) [W] | Calc: σ(P_lossConv) [W] | σ(P_loss) [W] | Calc: σ(P_loss) [W] | P_in [W] | P_sec [W] | P_lossTran [W] | P_lossConv [W] | P_loss [W] | Est. ΔP_in [W] | Conf. ΔP_in [W] | Est. ΔP_in/P_in [%] | Conf. ΔP_in/P_in [%] | Est. ΔP_sec [W] | Conf. ΔP_sec [W] | Est. ΔP_sec/P_sec [%] | Conf. ΔP_sec/P_sec [%] | Est. ΔP_lossTran [W] | Conf. ΔP_lossTran [W] | Est. ΔP_lossTran/P_lossTran [%] | Conf. ΔP_lossTran/P_lossTran [%] | Est. ΔP_lossConv [W] | Conf. ΔP_lossConv [W] | Est. ΔP_lossConv/P_lossConv [%] | Conf. ΔP_lossConv/P_lossConv [%] | Est. ΔP_loss [W] | Conf. ΔP_loss [W] | Est. ΔP_loss/P_loss [%] | Conf. ΔP_loss/P_loss [%]
1.1 | 18.9664 | 0.0024978 | 0.047374 | 0 | 18.6087 | 0.0034664 | 0.064505 | 0 | 18.7034 | 0.010471 | 0.19585 | 0 | 24.2465 | 0.040497 | 0.9819 | 0 | 24.1973 | 0.021442 | 0.51884 | 0 | 24.1836 | 0.041408 | 1.0014 | 0 | 48.1924 |  | 2.5806e-16 | 0 | 48.5563 |  | 2.6197e-16 | 0 | 48.1949 |  | 2.5808e-16 | 0 | 101.8254 | 50.3192 | 2.8099 | 0 | 51.5062 | 47.5093 | 50.3192 | 99.0155 | 101.8254 | 0.0024358 | 0.00017741 | 4.2855e-07 | 0.0033708 | 0 | 0.0017542 | 5.8958e-05 | -9.9294e-08 | 0.0010913 | 0 | 0.00035361 | 0.00013574 | 4.3372e-08 | 0.002542 | 0 | 0.0043774 | 0.00013498 | 5.4939e-07 | 0.0034379 | 0 | 0.0048981 | 0.00016277 | 7.6354e-07 | 0.0040391 | 0 | 0.0043774 | 0.00013498 | 5.4939e-07 | 0.0034379 | 0 | 0.00018776 | 0 | 2.0108e-21 | 0 | 0.0022979 | 0 | 2.4795e-20 | 0 | 0.0011349 | 0 | 1.2155e-20 | 0 | 0.10806 | 0.074343 | 0.010864 | 0.0076791 | 0.048791 | 0.085099 | 0.075133 | 0.11863 | 0.1086 | 99.2241 | 51.334 | 47.8901 | 51.244 | 99.1341 | -2.6013 | 0.18217 | -2.555% | 0.1789% | 1.0148 | 0.12533 | 2.017% | 0.2491% | -3.6161 | 0.082255 | -7.021% | 0.1597% | 0.92483 | 0.14346 | 1.838% | 0.2851% | -2.6913 | 0.19999 | -2.643% | 0.1964%
1.2 | 18.2864 | 3.9706 | 72.6085 | 72.6085 | 18.1998 | 3.915 | 71.2526 | 71.2526 | 18.2466 | 3.8867 | 70.9184 | 70.9184 | 24.1492 | 1.1655 | 28.1469 | 28.147 | 24.0675 | 1.1895 | 28.6288 | 28.629 | 24.0951 | 1.1478 | 27.6556 | 27.6557 | 48.1935 |  | 2.5807e-16 | 0 | 48.5702 |  | 2.6212e-16 | 0 | 48.198 |  | 2.5812e-16 | 0 | 460.7164 | 403.4319 | 299.2109 | 299.2112 | 57.2845 | 104.221 | 104.2207 | 161.5055 | 161.5052 | 0.0068116 | 0.0031036 | 2.1032e-05 | 0.083713 | 0.083706 | 0.0018585 | 0.0030489 | -5.539e-06 | 0.048408 | 0.0484 | 0.0012427 | 0.017933 | -1.1035e-05 | 0.32488 | 0.32486 | 0.0078779 | 0.020175 | -0.00015708 | 0.47818 | 0.47813 | 0.0087522 | 0.019001 | -0.00016457 | 0.44705 | 0.44701 | 0.0078779 | 0.020175 | -0.00015708 | 0.47818 | 0.47718 | 0.00081456 | 0 | 8.7237e-21 | 0 | 0.0094645 | 0 | 1.0216e-19 | 0 | 0.00070497 | 0 | 7.5507e-21 | 0 | 0.8643 | 0.85987 | 0.98138 | 0.87867 | 0.027825 | 0.12784 | 1.3048 | 0.11754 | 1.3077 | 449.2111 | 394.8065 | 54.4046 | 95.4285 | 149.8331 | -11.5053 | 1.4571 | -2.497% | 0.3163% | -8.6254 | 1.4496 | -2.138% | 0.3593% | -2.8799 | 0.046909 | -5.027% | 0.08189% | -8.7922 | 0.21551 | -8.436% | 0.2068% | -11.6721 | 0.19816 | -7.227% | 0.1227%
1.3 | 18.292 | 3.9734 | 72.6815 | 72.6815 | 18.2061 | 3.8754 | 70.5556 | 70.5556 | 18.2552 | 3.91 | 71.378 | 71.378 | 24.1545 | 1.158 | 27.9701 | 27.9701 | 24.0762 | 1.1752 | 28.2942 | 28.2942 | 24.1021 | 1.1345 | 27.3449 | 27.3449 | 48.191 | 10.044 | 231.3116 | 231.2195 | 48.3679 | 10.138 | 230.7157 | 230.7613 | 48.2073 | 9.807 | 236.895 | 236.9674 | 1254.8799 | 1172.1752 | 997.1466 | 997.1725 | 82.7047 | 175.0286 | 175.0027 | 257.7332 | 257.7074 | 0.00088171 | 0.00039715 | -2.1583e-07 | 0.0058027 | 0.005803 | 0.00098092 | 0.015498 | -2.7311e-06 | 0.28149 | 0.28149 | 0.014106 | 0.0028929 | 4.0301e-05 | 0.10763 | 0.10763 | 0.00094476 | 0.0014379 | -1.1013e-06 | 0.033851 | 0.03385 | 0.0025932 | 0.001694 | -4.3873e-06 | 0.037739 | 0.037741 | 0.00094476 | 0.0014379 | -1.1013e-06 | 0.033851 | 0.033793 | 0.00016833 | 0.0139 | 0.0016159 | 0.31999 | 0.0014007 | 0.0102 | 0.013363 | 0.23256 | 0.0006141 | 0.0086 | 0.0060355 | 0.20789 | 1.2576 | 0.95465 | 0.48537 | 0.54247 | 0.35192 | 1.3922 | 1.098 | 1.7173 | 1.3696 | 1243.6592 | 1161.3986 | 82.2606 | 165.2285 | 247.4891 | -11.2207 | 2.1201 | -0.8942% | 0.1689% | -10.7766 | 1.6094 | -0.9194% | 0.1373% | -0.44408 | 0.59328 | -0.5369% | 0.7173% | -9.7742 | 2.3471 | -5.585% | 1.341% | -10.2183 | 2.8951 | -3.965% | 1.123%
1.4 | 18.2919 | 3.9723 | 72.6606 | 72.6606 | 18.2004 | 3.8737 | 70.5023 | 70.5023 | 18.242 | 3.9061 | 71.2558 | 71.2558 | 24.1552 | 1.1612 | 28.0478 | 28.0479 | 24.0781 | 1.1785 | 28.3751 | 28.3752 | 24.1037 | 1.1372 | 27.4119 | 27.4119 | 48.1868 | 5.635 | 411.6969 | 412.0622 | 47.7719 | 5.645 | 404.6378 | 404.2794 | 48.1994 | 5.6 | 414.8546 | 414.8546 | 1870.8601 | 1750.2346 | 1529.4428 | 1529.4497 | 120.6256 | 220.7918 | 220.7848 | 341.4173 | 341.4104 | 0.0021292 | 0.00081867 | 4.3322e-07 | 0.018941 | 0.01894 | 0.002106 | 0.0034452 | 1.8413e-06 | 0.065248 | 0.065253 | 0.0021871 | 0.0003696 | -6.5615e-07 | 0.004991 | 0.0049932 | 0.0017711 | 0.0031653 | -5.5715e-06 | 0.074413 | 0.074414 | 0.0022703 | 0.0043008 | -9.6494e-06 | 0.10091 | 0.10091 | 0.0017711 | 0.0031653 | -5.5715e-06 | 0.074413 | 0.074293 | 0.00070525 | 0.0057 | 0.012051 | 0.41699 | 0.0001897 | 0.0041 | 0.0032135 | 0.29365 | 0.0010792 | 0.0131 | 0.018578 | 0.97064 | 1.03 | 0.59123 | 0.22563 | 1.1082 | 0.53934 | 0.48063 | 1.2561 | 0.83617 | 1.513 | 1887.9409 | 1749.9227 | 138.0182 | 220.8298 | 358.848 | 17.0807 | 1.7365 | 0.913% | 0.09282% | -0.31187 | 0.99673 | -0.01782% | 0.05695% | 17.3926 | 0.90925 | 14.42% | 0.7538% | 0.044957 | 0.81028 | 0.02036% | 0.367% | 17.4376 | 1.4097 | 5.108% | 0.4129%
2.1 | 18.9738 | 0.0026749 | 0.050754 | 0 | 18.6039 | 0.0035587 | 0.066206 | 0 | 18.7022 | 0.010343 | 0.19344 | 0 | 24.2576 | 0.040438 | 0.98092 | 0 | 24.2108 | 0.021475 | 0.51994 | 0 | 24.2048 | 0.041282 | 0.99922 | 0 | 48.1923 |  | 2.5805e-16 | 0 | 48.5527 |  | 2.6193e-16 | 0 | 48.192 |  | 2.5805e-16 | 0 | 101.5983 | 50.2957 | 2.8105 | 0 | 51.3026 | 47.4852 | 50.2957 | 98.7878 | 101.5983 | 0.0018911 | 1.0406e-05 | -2.1323e-09 | 0.00019696 | 0 | 0.0011902 | 6.5164e-05 | -1.9463e-08 | 0.0012113 | 0 | 0.00039309 | 1.1531e-05 | -1.9495e-09 | 0.00021395 | 0 | 0.0023162 | 0.00017587 | -3.082e-07 | 0.004196 | 0 | 0.0030142 | 0.00017047 | -2.6111e-07 | 0.0040946 | 0 | 0.0023162 | 0.00017587 | -3.082e-07 | 0.004196 | 0 | 0.00010411 | 0 | 1.115e-21 | 0 | 0.00030561 | 0 | 3.2973e-21 | 0 | 0.00081786 | 0 | 8.7587e-21 | 0 | 0.10255 | 0.011595 | 0.0040495 | 0.0073164 | 0.114 | 0.015569 | 0.01371 | 0.098505 | 0.10281 | 99.2241 | 51.334 | 47.8901 | 51.244 | 99.1341 | -2.3742 | 0.17288 | -2.337% | 0.1702% | 1.0383 | 0.019547 | 2.064% | 0.03886% | -3.4125 | 0.19218 | -6.652% | 0.3746% | 0.94834 | 0.026246 | 1.886% | 0.05218% | -2.4642 | 0.16607 | -2.425% | 0.1635%
2.2 | 18.2989 | 3.9717 | 72.6784 | 72.6784 | 18.18 | 3.8781 | 70.5034 | 70.5034 | 18.2348 | 3.9043 | 71.1938 | 71.1938 | 24.1774 | 1.1279 | 27.2695 | 27.2698 | 24.102 | 1.1556 | 27.8526 | 27.8528 | 24.1483 | 1.1066 | 26.7232 | 26.7236 | 48.1811 | 4.005 | 580.354 | 579.6295 | 48.5536 |  | 2.6194e-16 | 0 | 48.1987 | 4.15 | 559.7868 | 559.7868 | 1772.1047 | 1651.1076 | 1436.3617 | 1435.638 | 120.9971 | 214.7459 | 215.4696 | 335.743 | 336.4667 | 0.0055973 | 0.00082935 | 3.5829e-06 | 0.035287 | 0.035289 | 0.0034159 | 0.00054734 | -9.679e-08 | 0.01615 | 0.016151 | 0.0063548 | 0.00041071 | 4.3398e-07 | 0.027083 | 0.027083 | 0.012337 | 0.027413 | -0.00033662 | 0.64894 | 0.64893 | 0.013245 | 0.026552 | -0.00035167 | 0.62461 | 0.62465 | 0.012337 | 0.027413 | -0.00033662 | 0.64894 | 0.64839 | 0.00050469 | 0.0068 | 0.012158 | 0.98421 | 0.00096527 | 0 | 1.0415e-20 | 0 | 0.00036614 | 0.0079 | 0.0085049 | 1.0657 | 0.73695 | 1.5403 | 2.0202 | 1.8273 | 1.1112 | 3.5598 | 2.5404 | 2.6277 | 2.1504 | 1796.8604 | 1654.8773 | 141.9831 | 219.0028 | 360.986 | 24.7557 | 1.2424 | 1.397% | 0.07011% | 3.7697 | 2.5967 | 0.2283% | 0.1573% | 20.986 | 1.8733 | 17.34% | 1.548% | 3.5333 | 6.0014 | 1.64% | 2.785% | 24.5193 | 4.4299 | 7.287% | 1.317%
2.3 | 18.2953 | 3.9719 | 72.6673 | 72.6673 | 18.1893 | 3.8754 | 70.4904 | 70.4905 | 18.2424 | 3.91 | 71.3286 | 71.3286 | 24.1606 | 1.1485 | 27.7476 | 27.7477 | 24.0853 | 1.1753 | 28.3067 | 28.3067 | 24.1183 | 1.1277 | 27.1973 | 27.1973 | 48.1904 | 10.044 | 231.3065 | 231.2144 | 47.7712 | 5.645 | 404.626 | 404.2676 | 48.2031 | 4.15 | 559.89 | 559.89 | 1839.236 | 1709.4192 | 1493.5606 | 1493.1102 | 129.8168 | 215.8587 | 216.3091 | 345.6754 | 346.1259 | 0.00066044 | 0.00021666 | -4.0409e-08 | 0.0040889 | 0.004089 | 0.0042459 | 0.0050972 | -1.5852e-05 | 0.081423 | 0.081438 | 0.0018682 | 0.0018045 | 2.6587e-06 | 0.038938 | 0.038939 | 0.0036344 | 0.0067973 | -2.4626e-05 | 0.16007 | 0.16007 | 0.0040923 | 0.0059423 | -2.4229e-05 | 0.13834 | 0.13833 | 0.0036344 | 0.0067973 | -2.4626e-05 | 0.16007 | 0.15985 | 0.00024228 | 0.0139 | 0.0023258 | 0.31999 | 0.0032295 | 0.0041 | 0.054707 | 0.29867 | 0.0026267 | 0.0079 | 0.061019 | 1.0676 | 0.972 | 0.45981 | 0.46927 | 1.1874 | 0.51302 | 0.133 | 1.2733 | 0.52866 | 1.5345 | 1861.3645 | 1711.0427 | 150.3219 | 217.7413 | 368.0631 | 22.1285 | 1.6386 | 1.203% | 0.08909% | 1.6234 | 0.77518 | 0.09497% | 0.04535% | 20.5051 | 0.86488 | 15.8% | 0.6662% | 1.4322 | 0.22421 | 0.6621% | 0.1037% | 21.9372 | 0.89124 | 6.338% | 0.2575%
2.4 | 18.2945 | 3.9727 | 72.6786 | 72.6786 | 18.195 | 3.8736 | 70.4799 | 70.4799 | 18.2473 | 3.91 | 71.3479 | 71.3479 | 24.1602 | 1.1551 | 27.9067 | 27.9068 | 24.0833 | 1.1716 | 28.2153 | 28.2153 | 24.1109 | 1.1292 | 27.2249 | 27.225 | 48.1838 | 4.005 | 580.4201 | 579.6955 | 47.7793 | 5.645 | 404.7623 | 404.4038 | 48.1976 |  | 2.5811e-16 | 0 | 1583.8868 | 1482.2799 | 1283.0357 | 1281.9527 | 101.6069 | 199.2442 | 200.3272 | 300.8511 | 301.9342 | 0.0017099 | 0.00098804 | 1.3351e-06 | 0.023811 | 0.023811 | 0.0020715 | 0.006253 | -1.1454e-05 | 0.10673 | 0.10674 | 0.0019743 | 0.0031607 | 4.8658e-06 | 0.063863 | 0.063877 | 0.0044102 | 0.012422 | -5.4115e-05 | 0.2951 | 0.29509 | 0.0045343 | 0.011633 | -5.152e-05 | 0.27498 | 0.27496 | 0.0044102 | 0.012422 | -5.4115e-05 | 0.2951 | 0.29459 | 0.00051413 | 0.0068 | 0.012386 | 0.98433 | 0.001082 | 0.0041 | 0.018332 | 0.29429 | 0.0011576 | 0 | 1.2398e-20 | 0 | 0.6419 | 0.76336 | 0.58033 | 1.1495 | 0.185 | 1.3201 | 1.3799 | 1.1716 | 1.3166 | 1599.1943 | 1483.8534 | 115.3409 | 200.9747 | 316.3156 | 15.3075 | 1.0822 | 0.9664% | 0.06832% | 1.5735 | 1.2869 | 0.1062% | 0.08682% | 13.734 | 0.31189 | 13.52% | 0.307% | 0.64747 | 2.2255 | 0.3232% | 1.111% | 14.3814 | 1.9751 | 4.763% | 0.6542%
[94 empty] | This data is from simulations for a simplified transformer model (Ignoring nonlinear terms) Scenario 1 Dataset 1.3 |  |  | 1243.6476 | 1161.3986 | 82.249 | 165.2285 | 247.4775
[44 empty] | ` | [49 empty] | Unsymmetric transformer model (with nonlinear terms) |  |  | 1277.5386 | 1161.3986 | 116.1399 | 165.2285 | 281.3685
[94 empty] | Unsymmetric transformer model (ignoring nonlinear terms) |  |  | 1249.3076 | 1161.3986 | 87.909 | 165.2285 | 253.1375
Note on E4: Setting to zero
Note on E8: Setting to zero
Note on I4: Setting to zero
Note on I8: Setting to zero
Note on M4: Setting to zero
Note on M8: Setting to zero
Note on Q4: Setting to zero
Note on Q8: Setting to zero
Note on U4: Setting to zero
Note on U8: Setting to zero
Note on Y4: Setting to zero
Note on Y8: Setting to zero
Note on AA4: Open circuit
Note on AA5: Open circuit
Note on AA6: 10Ω Resistor A See 'Resistor Values' spreadsheet
Note on AA7: 5.6Ω Resistor A See 'Resistor Values' spreadsheet
Note on AA8: Open circuit
Note on AA9: 3.9Ω Resistor A See 'Resistor Values' spreadsheet
Note on AA10: 10Ω Resistor A See 'Resistor Values' spreadsheet
Note on AA11: 3.9Ω Resistor A See 'Resistor Values' spreadsheet
Note on AE4: Open circuit
Note on AE5: Open circuit
Note on AE6: 10Ω Resistor B See 'Resistor Values' spreadsheet
Note on AE7: 5.6Ω Resistor B See 'Resistor Values' spreadsheet
Note on AE8: Open circuit
Note on AE9: Open circuit
Note on AE10: 5.6Ω Resistor B See 'Resistor Values' spreadsheet
Note on AE11: 5.6Ω Resistor B See 'Resistor Values' spreadsheet
Note on AI4: Open circuit
Note on AI5: Open circuit
Note on AI6: 10Ω Resistor A See 'Resistor Values' spreadsheet
Note on AI7: 5.6Ω Resistor C See 'Resistor Values' spreadsheet
Note on AI8: Open circuit
Note on AI9: 3.9Ω Resistor C See 'Resistor Values' spreadsheet
Note on AI10: 3.9Ω Resistor C See 'Resistor Values' spreadsheet
Note on AI11: Open circuit
Note on AY3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html Includes covariances for P=V*I loads
Note on BD3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html Includes covariances for P=V*I loads
Note on BI3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html Includes covariances for P=V*I loads
Note on BN3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html Includes covariances for P=V*I loads
Note on BS3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html Includes covariances for P=V*I loads
Note on BX3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html Includes covariances for P=V*I loads
Note on BZ4: Open circuit
Note on BZ5: Open circuit
Note on BZ6: 10Ω Resistor A See 'Resistor Values' spreadsheet
Note on BZ7: 5.6Ω Resistor A See 'Resistor Values' spreadsheet
Note on BZ8: Open circuit
Note on BZ9: 3.9Ω Resistor A See 'Resistor Values' spreadsheet
Note on BZ10: 10Ω Resistor A See 'Resistor Values' spreadsheet
Note on BZ11: 3.9Ω Resistor A See 'Resistor Values' spreadsheet
Note on CB3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html
Note on CD4: Open circuit
Note on CD5: Open circuit
Note on CD6: 10Ω Resistor B See 'Resistor Values' spreadsheet
Note on CD7: 5.6Ω Resistor B See 'Resistor Values' spreadsheet
Note on CD8: Open circuit
Note on CD9: Open circuit
Note on CD10: 5.6Ω Resistor B See 'Resistor Values' spreadsheet
Note on CD11: 5.6Ω Resistor B See 'Resistor Values' spreadsheet
Note on CF3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html
Note on CH4: Open circuit
Note on CH5: Open circuit
Note on CH6: 10Ω Resistor C See 'Resistor Values' spreadsheet
Note on CH7: 5.6Ω Resistor C See 'Resistor Values' spreadsheet
Note on CH8: Open circuit
Note on CH9: 3.9Ω Resistor C See 'Resistor Values' spreadsheet
Note on CH10: 3.9Ω Resistor C See 'Resistor Values' spreadsheet
Note on CH11: Open circuit
Note on CJ3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html
Note on CN3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html Uses measured variances for V*I loads, calculated variances for V²/R loads. Provided for cross-check ONLY.
Note on CQ3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html Uses maximum of calculated or observed variance for P_out. Provided for cross-check ONLY.
Note on CS3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html Uses maximum of calculated or observed variance for P_out. Provided for cross-check ONLY.
Note on CY1: Calculations follow eq. (7), (8), and (15) from doi:10.1016/j.jcp.2006.03.037. Calculated assuming each run is an independent experiment that yields a single sample with estimate of all relevant quantities (the mean value). Thus, for three runs: n = 3 ν = 3 - 1 = 2 Note this yields much larger confidence intervals than an alternative approach where each 5-second interval is considered a single experiment/sample.
Note on CZ3: Note that the sample standard deviation s(ΔP_in) = s(P_in), because the modeled value is fixed. Same for the other confidence interval calculations.

## Scenarios 3-4
Scenarios 3-4: AC Balanced, Unbalanced + Heaters | [118 empty] | Model Results |  |  |  |  | Estimates of Error (90% Confidence Interval)
Metadata | Load: Laptop Charger 3 |  |  |  | Load: Laptop Charger 4 |  |  |  | Load: Laptop Charger 5 |  |  |  | Load: LED 1 |  |  |  | Load: LED 2 |  |  |  | Load: LED 3 |  |  |  | Heater 1-A |  |  |  | Heater 1-B |  |  |  | Heater 1-C |  |  |  | Heater 2-A |  |  |  | Heater 2-B |  |  |  | Heater 2-C |  |  |  | Input | Trans. Secondary | Output |  | Loss |  |  | Load: Laptop Charger 3 |  |  |  |  | Load: Laptop Charger 4 |  |  |  |  | Load: Laptop Charger 5 |  |  |  |  | Load: LED 1 |  |  |  |  | Load: LED 2 |  |  |  |  | Load: LED 3 |  |  |  |  | Heater 1-A |  |  |  | Heater 1-B |  |  |  | Heater 1-C |  |  |  | Heater 2-A |  |  |  | Heater 2-B |  |  |  | Heater 2-C |  |  |  | Input | Trans. Secondary | Output |  | Loss |  |  |  |  | Power Values |  |  |  |  | Input Power: P_in |  |  |  | Transformer Secondary Power: P_sec |  |  |  | Transformer Loss: P_lossTran |  |  |  | Converter Loss: P_lossConv |  |  |  | System Loss: P_loss
Data Set | V_load [V] | I_load [A] | P_load [W] | Calc: P_load [W] | V_load [V] | I_load [A] | P_load [W] | Calc: P_load [W] | V_load [V] | I_load [A] | P_load [W] | Calc: P_load [W] | V_load [V] | I_load [A] | P_load [W] | Calc: P_load [W] | V_load [V] | I_load [A] | P_load [W] | Calc: P_load [W] | V_load [V] | I_load [A] | P_load [W] | Calc: P_load [W] | V_load [V] | g_load [℧] | P_load [W] | Calc: P_load [W] | V_load [V] | g_load [℧] | P_load [W] | Calc: P_load [W] | V_load [V] | g_load [℧] | P_load [W] | Calc: P_load [W] | V_load [V] | g_load [℧] | P_load [W] | Calc: P_load [W] | V_load [V] | g_load [℧] | P_load [W] | Calc: P_load [W] | V_load [V] | g_load [℧] | P_load [W] | Calc: P_load [W] | P_in [W] | P_sec [W] | P_out [W] | Calc: P_out [W] | P_lossTran [W] | P_lossConv [W] | P_loss [W] | σ(V_load) [V] | σ(I_load) [A] | COV(V_load,I_load) [(VA)²] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(I_load) [A] | COV(V_load,I_load) [(VA)²] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(I_load) [A] | COV(V_load,I_load) [(VA)²] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(I_load) [A] | COV(V_load,I_load) [(VA)²] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(I_load) [A] | COV(V_load,I_load) [(VA)²] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(I_load) [A] | COV(V_load,I_load) [(VA)²] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(g_load) [℧] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(g_load) [℧] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(g_load) [℧] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(g_load) [℧] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(g_load) [℧] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(g_load) [℧] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(P_in) [W] | σ(P_sec) [W] | σ(P_out) [W] | Calc: σ(P_out) [W] | σ(P_lossTran) [W] | σ(P_lossConv) [W] | Calc: σ(P_lossConv) [W] | σ(P_loss) [W] | Calc: σ(P_loss) [W] | P_in [W] | P_sec [W] | P_lossTran [W] | P_lossConv [W] | P_loss [W] | Est. ΔP_in [W] | Conf. ΔP_in [W] | Est. ΔP_in/P_in [%] | Conf. ΔP_in/P_in [%] | Est. ΔP_sec [W] | Conf. ΔP_sec [W] | Est. ΔP_sec/P_sec [%] | Conf. ΔP_sec/P_sec [%] | Est. ΔP_lossTran [W] | Conf. ΔP_lossTran [W] | Est. ΔP_lossTran/P_lossTran [%] | Conf. ΔP_lossTran/P_lossTran [%] | Est. ΔP_lossConv [W] | Conf. ΔP_lossConv [W] | Est. ΔP_lossConv/P_lossConv [%] | Conf. ΔP_lossConv/P_lossConv [%] | Est. ΔP_loss [W] | Conf. ΔP_loss [W] | Est. ΔP_loss/P_loss [%] | Conf. ΔP_loss/P_loss [%]
3.1 | 18.9853 | 0.0028257 | 0.053646 | 0 | 18.5954 | 0.0036672 | 0.068194 | 0 | 18.6993 | 0.010017 | 0.18731 | 0 | 24.2664 | 0.040784 | 0.98967 | 0 | 24.225 | 0.021713 | 0.526 | 0 | 24.2316 | 0.041589 | 1.0078 | 0 | 122.938 | 0 | 0 | 0 | 122.6806 | 0 | 0 | 0 | 122.8926 | 0 | 0 | 0 | 122.938 | 0 | 0 | 0 | 122.6806 | 0 | 0 | 0 | 122.8926 | 0 | 0 | 0 | 56.777 | 5.2928 | 2.8326 | 0 | 51.4841 | 2.4603 | 53.9444 | 0.00017131 | 8.8532e-05 | 1.4769e-08 | 0.0016813 | 0.0016813 | 0.00029634 | 1.7523e-05 | -2.6094e-09 | 0.00032531 | 0.00032531 | 9.1779e-05 | 0.00011261 | 1.024e-08 | 0.0021067 | 0.0021067 | 0.00061679 | 6.0056e-05 | -5.1321e-09 | 0.0014541 | 0.0014541 | 0.00065095 | 0.00012804 | -7.7998e-08 | 0.0030886 | 0.0030887 | 0.00061679 | 6.0056e-05 | -5.1321e-09 | 0.0014541 | 0.0014519 | 0.090977 | 0 | 0 | 0 | 0.093604 | 0 | 0 | 0 | 0.095685 | 0 | 0 | 0 | 0.090977 | 0 | 0 | 0 | 0.093604 | 0 | 0 | 0 | 0.095685 | 0 | 0 | 0 | 0.11366 | 0.004456 | 0.004564 | 0.0045977 | 0.10969 | 0.0070223 | 0.0064028 | 0.11656 | 0.11376 | 56.1849 | 8.1517 | 48.0332 | 5.3187 | 53.3519 | -0.59205 | 0.19162 | -1.043% | 0.3375% | 2.8589 | 0.0075122 | 54.01% | 0.1419% | -3.4509 | 0.18492 | -6.703% | 0.3592% | 2.8585 | 0.011838 | 116.2% | 0.4812% | -0.59247 | 0.19651 | -1.098% | 0.3643%
3.2 | 18.2803 | 3.9751 | 72.6664 | 72.6663 | 18.1692 | 3.9004 | 70.8667 | 70.8667 | 18.2254 | 3.8621 | 70.3883 | 70.3884 | 24.166 | 1.1424 | 27.6065 | 27.6067 | 24.0985 | 1.1805 | 28.4491 | 28.4494 | 24.1328 | 1.1443 | 27.615 | 27.6155 | 123.2738 | 0 | 0 | 0 | 123.1524 | 0 | 0 | 0 | 123.3594 | 0 | 0 | 0 | 123.2738 | 0 | 0 | 0 | 123.1524 | 0 | 0 | 0 | 123.3594 | 0 | 0 | 0 | 415.3043 | 357.6343 | 297.5919 | 297.5929 | 57.67 | 60.0424 | 117.7124 | 0.0023311 | 0.0011934 | 2.7548e-06 | 0.031018 | 0.031019 | 0.0027701 | 0.00065909 | -1.8138e-06 | 0.0017493 | 0.0017504 | 0.0088442 | 0.0075816 | -5.4538e-05 | 0.11215 | 0.11217 | 0.014333 | 0.021836 | -0.0003071 | 0.51178 | 0.51163 | 0.016972 | 0.025366 | -0.00042769 | 0.59153 | 0.59137 | 0.014333 | 0.021836 | -0.0003071 | 0.51178 | 0.51088 | 0.051596 | 0 | 0 | 0 | 0.078766 | 0 | 0 | 0 | 0.056822 | 0 | 0 | 0 | 0.051596 | 0 | 0 | 0 | 0.078766 | 0 | 0 | 0 | 0.056822 | 0 | 0 | 0 | 1.0964 | 1.0606 | 1.6742 | 0.94196 | 0.048949 | 0.61364 | 1.9818 | 0.57977 | 2.0012 | 400.4323 | 346.7806 | 53.6517 | 49.1896 | 102.8413 | -14.872 | 1.8484 | -3.581% | 0.4451% | -10.8537 | 1.7879 | -3.035% | 0.4999% | -4.0183 | 0.082521 | -6.968% | 0.1431% | -10.8528 | 1.0345 | -18.08% | 1.723% | -14.8711 | 0.97741 | -12.63% | 0.8303%
3.3 | 18.1988 | 3.8839 | 70.6827 | 70.6828 | 18.2435 | 3.8684 | 70.5733 | 70.5733 | 18.3022 | 3.677 | 67.2974 | 67.2974 | 24.1048 | 1.1994 | 28.9104 | 28.9104 | 24.0072 | 1.2046 | 28.9197 | 28.9197 | 24.0311 | 1.1688 | 28.0883 | 28.0884 | 121.9879 | 0.012693 | 193.1047 | 188.8852 | 121.7741 | 0.011647 | 179.9577 | 172.7125 | 122.0283 | 0.012295 | 185.5727 | 183.0838 | 121.9879 | 0 | 0 | 0 | 121.7741 | 0 | 0 | 0 | 122.0283 | 0 | 0 | 0 | 985.3049 | 919.3274 | 853.1069 | 839.1535 | 65.9774 | 66.2205 | 132.1979 | 0.01218 | 0.0064515 | -4.7149e-05 | 0.09669 | 0.096736 | 0.0029773 | 0.00035026 | 8.3271e-07 | 0.017063 | 0.017059 | 0.0013961 | 0.010776 | 1.5039e-05 | 0.20234 | 0.20235 | 0.0066143 | 0.0077774 | -5.144e-05 | 0.17957 | 0.17954 | 0.0063645 | 0.0072123 | -4.5903e-05 | 0.1655 | 0.16548 | 0.0066143 | 0.0077774 | -5.144e-05 | 0.17957 | 0.17917 | 0.10168 | 2.3e-05 | 0.20542 | 0.46507 | 0.13256 | 1.2e-05 | 0.19348 | 0.41601 | 0.11035 | 2.2e-05 | 0.12864 | 0.4658 | 0.10168 | 0 | 0 | 0 | 0.13256 | 0 | 0 | 0 | 0.11035 | 0 | 0 | 0 | 0.17861 | 0.15027 | 0.35417 | 0.48851 | 0.082076 | 0.21655 | 0.5111 | 0.26167 | 0.52014 | 966.1797 | 901.8782 | 64.3015 | 48.7712 | 113.0727 | -19.1252 | 0.30112 | -1.941% | 0.03056% | -17.4492 | 0.25334 | -1.898% | 0.02756% | -1.6759 | 0.13837 | -2.54% | 0.2097% | -17.4493 | 0.36506 | -26.35% | 0.5513% | -19.1252 | 0.44114 | -14.47% | 0.3337%
3.4 | 18.1931 | 3.8844 | 70.6685 | 70.6685 | 18.2467 | 3.863 | 70.4878 | 70.4878 | 18.3065 | 3.6848 | 67.4558 | 67.4558 | 24.0962 | 1.2131 | 29.2318 | 29.2318 | 23.995 | 1.2097 | 29.0265 | 29.0265 | 24.017 | 1.1729 | 28.1705 | 28.1705 | 121.0365 | 0 | 0 | 0 | 120.7164 | 0 | 0 | 0 | 120.9824 | 0 | 0 | 0 | 121.0365 | 0.026068 | 384.698 | 381.8917 | 120.7164 | 0.026084 | 384.8435 | 380.1075 | 120.9824 | 0.026594 | 397.6113 | 389.2495 | 1613.1601 | 1529.1629 | 1462.1936 | 1446.2896 | 83.9972 | 66.9693 | 150.9665 | 0.0019834 | 0.0025677 | -7.2257e-07 | 0.046257 | 0.046254 | 0.00048913 | 0.0016106 | 7.2919e-07 | 0.031145 | 0.031146 | 0.0014417 | 0.013887 | -1.9972e-05 | 0.24893 | 0.24892 | 0.00080164 | 9.694e-05 | 5.8754e-08 | 0.0031364 | 0.0031364 | 0.00059626 | 0.00058784 | -3.4649e-07 | 0.013393 | 0.013393 | 0.00080164 | 9.694e-05 | 5.8754e-08 | 0.0031364 | 0.0031008 | 0.04483 | 0 | 0 | 0 | 0.083427 | 0 | 0 | 0 | 0.042095 | 0 | 0 | 0 | 0.04483 | 4.7e-05 | 0.34735 | 0.74439 | 0.083427 | 3.3e-05 | 1.3224 | 0.71224 | 0.042095 | 3.5e-05 | 0.77471 | 0.57949 | 2.66 | 2.6304 | 2.4956 | 1.5921 | 0.094718 | 0.13487 | 3.6259 | 0.18419 | 3.6474 | 1598.8306 | 1511.0982 | 87.7323 | 48.9042 | 136.6366 | -14.3295 | 4.4843 | -0.8883% | 0.278% | -18.0646 | 4.4345 | -1.181% | 0.29% | 3.7351 | 0.15968 | 4.447% | 0.1901% | -18.0651 | 0.22737 | -26.98% | 0.3395% | -14.3299 | 0.31052 | -9.492% | 0.2057%
4.1 | 18.9857 | 0.0027335 | 0.051897 | 0 | 18.5948 | 0.003676 | 0.068355 | 0 | 18.6991 | 0.0099704 | 0.18644 | 0 | 24.2653 | 0.040919 | 0.99291 | 0 | 24.2238 | 0.021732 | 0.52643 | 0 | 24.2292 | 0.041563 | 1.007 | 0 | 122.9866 | 0 | 0 | 0 | 122.7308 | 0 | 0 | 0 | 122.9615 | 0 | 0 | 0 | 122.9866 | 0 | 0 | 0 | 122.7308 | 0 | 0 | 0 | 122.9615 | 0 | 0 | 0 | 56.7944 | 5.2752 | 2.8331 | 0 | 51.5192 | 2.4421 | 53.9613 | 0.00012082 | 2.9869e-05 | 1.3054e-09 | 0.0005672 | 0.0005672 | 0.00022474 | 2.2966e-05 | -5.2455e-10 | 0.00042696 | 0.00042696 | 0.00014627 | 0.00013243 | 6.5241e-09 | 0.0024768 | 0.0024768 | 0.00011055 | 0.00010904 | 1.1196e-08 | 0.00265 | 0.00265 | 0.00021283 | 0.0001923 | -2.9585e-08 | 0.0046549 | 0.004655 | 0.00011055 | 0.00010904 | 1.1196e-08 | 0.00265 | 0.0026462 | 0.039657 | 0 | 0 | 0 | 0.016779 | 0 | 0 | 0 | 0.013629 | 0 | 0 | 0 | 0.039657 | 0 | 0 | 0 | 0.016779 | 0 | 0 | 0 | 0.013629 | 0 | 0 | 0 | 0.036649 | 0.006255 | 0.0004296 | 0.0065079 | 0.034246 | 0.0066268 | 0.0090265 | 0.037015 | 0.037222 | 56.1859 | 8.1527 | 48.0332 | 5.3207 | 53.3539 | -0.60845 | 0.061785 | -1.071% | 0.1088% | 2.8775 | 0.010545 | 54.55% | 0.1999% | -3.486 | 0.057733 | -6.766% | 0.1121% | 2.8786 | 0.011172 | 117.9% | 0.4575% | -0.60739 | 0.062402 | -1.126% | 0.1156%
4.2 | 18.2069 | 3.8763 | 70.5752 | 70.5752 | 18.2474 | 3.8778 | 70.7599 | 70.7599 | 18.3192 | 3.6051 | 66.0423 | 66.0423 | 24.0945 | 1.2149 | 29.2725 | 29.2725 | 23.9924 | 1.2112 | 29.0591 | 29.0591 | 24.0143 | 1.1853 | 28.4648 | 28.4648 | 120.413 | 0.012693 | 192.8542 | 184.0395 | 122.7267 | 0 | 0 | 0 | 120.339 | 0.012295 | 189.2272 | 178.0497 | 120.413 | 0.026068 | 383.7741 | 377.9675 | 122.7267 | 0 | 0 | 0 | 120.339 | 0.026594 | 394.7179 | 385.1203 | 1616.6636 | 1522.8088 | 1454.7472 | 1419.351 | 93.8548 | 68.0616 | 161.9164 | 0.0033563 | 0.0018704 | 5.6835e-06 | 0.046165 | 0.046165 | 0.00052144 | 0.0014037 | 2.237e-07 | 0.026303 | 0.026303 | 0.0011944 | 0.027844 | -3.0262e-05 | 0.5062 | 0.50617 | 0.00049244 | 0.00088639 | -4.1988e-07 | 0.020782 | 0.020782 | 0.00041496 | 0.00036382 | -1.4769e-07 | 0.0082379 | 0.0082379 | 0.00049244 | 0.00088639 | -4.1988e-07 | 0.020782 | 0.020725 | 0.13772 | 2.3e-05 | 0.57336 | 0.53707 | 0.21482 | 0 | 0 | 0 | 0.13636 | 2.2e-05 | 0.3495 | 0.51412 | 0.13772 | 4.7e-05 | 0.19879 | 1.1009 | 0.21482 | 0 | 0 | 0 | 0.13636 | 3.5e-05 | 0.15615 | 1.0093 | 1.9491 | 1.6131 | 1.6317 | 0.88022 | 0.38882 | 0.090648 | 2.2945 | 0.33262 | 2.5419 | 1602.3582 | 1503.5603 | 98.7978 | 48.8143 | 147.6122 | -14.3054 | 3.2859 | -0.8849% | 0.2032% | -19.2484 | 2.7195 | -1.264% | 0.1786% | 4.943 | 0.6555 | 5.267% | 0.6984% | -19.2473 | 0.15282 | -28.28% | 0.2245% | -14.3043 | 0.56075 | -8.834% | 0.3463%
4.3 | 18.2069 | 3.8734 | 70.522 | 70.522 | 18.2472 | 3.8821 | 70.8371 | 70.8371 | 18.3332 | 3.5719 | 65.4842 | 65.4844 | 24.0928 | 1.2156 | 29.288 | 29.288 | 23.9922 | 1.2133 | 29.1091 | 29.1091 | 24.0134 | 1.1844 | 28.4403 | 28.4403 | 122.5017 | 0.012693 | 193.3498 | 190.4797 | 121.4252 | 0 | 0 | 0 | 120.5119 | 0.012295 | 188.9508 | 178.5619 | 122.5017 | 0 | 0 | 0 | 121.4252 | 0.026084 | 384.6737 | 384.5848 | 120.5119 | 0.026594 | 396.2564 | 386.2281 | 1612.942 | 1523.3708 | 1456.9114 | 1433.5353 | 89.5712 | 66.4594 | 156.0306 | 0.0021262 | 0.0060762 | 8.7101e-06 | 0.11634 | 0.11634 | 0.00030299 | 0.00061947 | 1.8481e-07 | 0.012463 | 0.012463 | 0.0020257 | 0.025891 | -4.1262e-05 | 0.46897 | 0.46899 | 0.00012941 | 0.0013115 | -1.573e-07 | 0.031453 | 0.031453 | 0.00028035 | 0.00028064 | 1.354e-08 | 0.0068 | 0.0068 | 0.00012941 | 0.0013115 | -1.573e-07 | 0.031453 | 0.031352 | 0.091639 | 2.3e-05 | 0.033198 | 0.4476 | 0.017696 | 0 | 0 | 0 | 0.033116 | 2.2e-05 | 0.23391 | 0.33424 | 0.091639 | 0 | 0 | 0 | 0.017696 | 3.3e-05 | 0.6328 | 0.4993 | 0.033116 | 3.5e-05 | 0.34142 | 0.55085 | 0.48413 | 0.56949 | 0.71261 | 0.89915 | 0.26381 | 0.15811 | 1.0643 | 0.31624 | 1.0212 | 1596.9125 | 1505.6463 | 91.2662 | 48.7353 | 140.0015 | -16.0295 | 0.81618 | -0.9938% | 0.0506% | -17.7245 | 0.96008 | -1.164% | 0.06302% | 1.695 | 0.44474 | 1.892% | 0.4965% | -17.7241 | 0.26655 | -26.67% | 0.4011% | -16.0291 | 0.53314 | -10.27% | 0.3417%
4.4 | 18.2023 | 3.8721 | 70.4809 | 70.4809 | 18.2476 | 3.8806 | 70.8126 | 70.8126 | 18.3336 | 3.5891 | 65.8013 | 65.8014 | 24.0958 | 1.2171 | 29.3258 | 29.3258 | 23.9912 | 1.2141 | 29.1271 | 29.1271 | 24.0101 | 1.1846 | 28.4429 | 28.4429 | 120.7623 | 0.012693 | 193.1082 | 185.1087 | 121.4168 | 0 | 0 | 0 | 123.5608 | 0 | 0 | 0 | 120.7623 | 0.026068 | 384.3622 | 380.1635 | 121.4168 | 0.026084 | 383.6185 | 384.5311 | 123.5608 | 0 | 0 | 0 | 1407.0337 | 1322.4505 | 1255.0794 | 1243.7939 | 84.5832 | 67.3711 | 151.9543 | 0.002506 | 0.001729 | -6.2413e-07 | 0.031568 | 0.031569 | 0.00015941 | 0.00085859 | -1.3681e-07 | 0.015049 | 0.015049 | 0.0022923 | 0.01897 | -4.2978e-05 | 0.33965 | 0.33965 | 0.0021652 | 0.000335 | 6.7091e-07 | 0.010557 | 0.010557 | 0.00017867 | 9.9735e-05 | -9.0991e-09 | 0.0022896 | 0.0022896 | 0.0021652 | 0.000335 | 6.7091e-07 | 0.010557 | 0.010461 | 0.22687 | 2.3e-05 | 0.18899 | 0.77216 | 0.166 | 0 | 0 | 0 | 0.22405 | 0 | 0 | 0 | 0.22687 | 4.7e-05 | 1.4735 | 1.5843 | 0.166 | 3.3e-05 | 0.45095 | 1.1586 | 0.22405 | 0 | 0 | 0 | 2.2776 | 2.3659 | 2.3792 | 1.5897 | 0.17188 | 0.039312 | 3.3553 | 0.21034 | 3.2937 | 1391.1464 | 1303.8635 | 87.2829 | 48.7845 | 136.0674 | -15.8873 | 3.8397 | -1.129% | 0.2729% | -18.587 | 3.9885 | -1.405% | 0.3016% | 2.6997 | 0.28977 | 3.192% | 0.3426% | -18.5866 | 0.066274 | -27.59% | 0.09837% | -15.8869 | 0.35461 | -10.46% | 0.2334%
Check
[53 empty] | Loss | [67 empty] | Loss
[53 empty] | P_lossTran [W] | P_lossConv [W] | P_loss [W] | [65 empty] | P_lossTran [W] | P_lossConv [W] | P_loss [W]
[53 empty] | 51.4841 | 2.4603 | 53.9444 | [65 empty] | 51.4841 | 2.4603 | 53.9444
| 3.1 | 3.2 | 3.3 | 3.4 | 4.1 | 4.2 | 4.3 | 4.4 | [44 empty] | 57.67 | 60.0424 | 117.7124 | [65 empty] | 57.67 | 60.0424 | 117.7124
Load: Laptop Charger 3 | 0.053646 | 72.6664 | 70.6827 | 70.6685 | 0.051897 | 70.5752 | 70.522 | 70.4809 | [44 empty] | 65.9774 | 66.2205 | 132.1979 | [65 empty] | 65.9774 | 66.2205 | 132.1979
Load: Laptop Charger 4 | 0.068194 | 70.8667 | 70.5733 | 70.4878 | 0.068355 | 70.7599 | 70.8371 | 70.8126 | [44 empty] | 83.9972 | 66.9693 | 150.9665 | [65 empty] | 83.9972 | 66.9693 | 150.9665
Load: Laptop Charger 5 | 0.18731 | 70.3883 | 67.2974 | 67.4558 | 0.18644 | 66.0423 | 65.4842 | 65.8013 | [44 empty] | 51.5192 | 2.4421 | 53.9613 | [65 empty] | 51.5192 | 2.4421 | 53.9613
LED 1 | 0.98967 | 27.6065 | 28.9104 | 29.2318 | 0.99291 | 29.2725 | 29.288 | 29.3258 | [44 empty] | 93.8548 | 68.0616 | 161.9164 | [65 empty] | 93.8548 | 68.0616 | 161.9164
LED 2 | 0.526 | 28.4491 | 28.9197 | 29.0265 | 0.52643 | 29.0591 | 29.1091 | 29.1271 | [44 empty] | 89.5712 | 66.4594 | 156.0306 | [65 empty] | 89.5712 | 66.4594 | 156.0306
LED 3 | 1.0078 | 27.615 | 28.0883 | 28.1705 | 1.007 | 28.4648 | 28.4403 | 28.4429 | [44 empty] | 84.5832 | 67.3711 | 151.9543 | [65 empty] | 84.5832 | 67.3711 | 151.9543
Heater 1-A | 0 | 0 | 193.1047 | 0 | 0 | 192.8542 | 193.3498 | 193.1082
Heater 1-B | 0 | 0 | 179.9577 | 0 | 0 | 0 | 0 | 0
Heater 1-C | 0 | 0 | 185.5727 | 0 | 0 | 189.2272 | 188.9508 | 0
Heater 2-A | 0 | 0 | 0 | 384.698 | 0 | 383.7741 | 0 | 384.3622
Heater 2-B | 0 | 0 | 0 | 384.8435 | 0 | 0 | 384.6737 | 383.6185
Heater 2-C | 0 | 0 | 0 | 397.6113 | 0 | 394.7179 | 396.2564 | 0
Output power (Calc) | 2.8326 | 297.5919 | 853.1069 | 1462.1936 | 2.8331 | 1454.7472 | 1456.9114 | 1255.0794
Check Output Power | 2.8326 | 297.5919 | 853.1069 | 1462.1936 | 2.8331 | 1454.7472 | 1456.9114 | 1255.0794
Note on B18: Avpreet: using OFFSET() to set references
Note on E4: Setting to zero
Note on E8: Setting to zero
Note on I4: Setting to zero
Note on I8: Setting to zero
Note on M4: Setting to zero
Note on M8: Setting to zero
Note on Q4: Setting to zero
Note on Q8: Setting to zero
Note on U4: Setting to zero
Note on U8: Setting to zero
Note on Y4: Setting to zero
Note on Y8: Setting to zero
Note on AA3: Equivalent conductance, per series admittance model.
Note on AA4: Open circuit
Note on AA5: Open circuit
Note on AA6: See 'Resistor Values' spreadsheet
Note on AA7: Open circuit
Note on AA8: Open circuit
Note on AA9: See 'Resistor Values' spreadsheet
Note on AA10: See 'Resistor Values' spreadsheet
Note on AA11: See 'Resistor Values' spreadsheet
Note on AC3: In updated experiments, heater power was measured directly using WEMO smart plugs. This is a more reliable power measurement method than the V^2/R calculation because heater power draw is known to vary slightly in response to controls. Calculated heater power is retained as a cross-check ONLY.
Note on AE3: Equivalent conductance, per series admittance model.
Note on AE4: Open circuit
Note on AE5: Open circuit
Note on AE6: See 'Resistor Values' spreadsheet
Note on AE7: Open circuit
Note on AE8: Open circuit
Note on AE9: Open circuit
Note on AE10: Open circuit
Note on AE11: Open circuit
Note on AG3: In updated experiments, heater power was measured directly using WEMO smart plugs. This is a more reliable power measurement method than the V^2/R calculation because heater power draw is known to vary slightly in response to controls. Calculated heater power is retained as a cross-check ONLY.
Note on AI3: Equivalent conductance, per series admittance model.
Note on AI4: Open circuit
Note on AI5: Open circuit
Note on AI6: See 'Resistor Values' spreadsheet
Note on AI7: Open circuit
Note on AI8: Open circuit
Note on AI9: See 'Resistor Values' spreadsheet
Note on AI10: See 'Resistor Values' spreadsheet
Note on AI11: Open circuit
Note on AK3: In updated experiments, heater power was measured directly using WEMO smart plugs. This is a more reliable power measurement method than the V^2/R calculation because heater power draw is known to vary slightly in response to controls. Calculated heater power is retained as a cross-check ONLY.
Note on AM3: Equivalent conductance, per series admittance model.
Note on AM4: Open circuit
Note on AM5: Open circuit
Note on AM6: Open circuit
Note on AM7: See 'Resistor Values' spreadsheet
Note on AM8: Open circuit
Note on AM9: See 'Resistor Values' spreadsheet
Note on AM10: Open circuit
Note on AM11: See 'Resistor Values' spreadsheet
Note on AO3: In updated experiments, heater power was measured directly using WEMO smart plugs. This is a more reliable power measurement method than the V^2/R calculation because heater power draw is known to vary slightly in response to controls. Calculated heater power is retained as a cross-check ONLY.
Note on AQ3: Equivalent conductance, per series admittance model.
Note on AQ4: Open circuit
Note on AQ5: Open circuit
Note on AQ6: Open circuit
Note on AQ7: See 'Resistor Values' spreadsheet
Note on AQ8: Open circuit
Note on AQ9: Open circuit
Note on AQ10: See 'Resistor Values' spreadsheet
Note on AQ11: See 'Resistor Values' spreadsheet
Note on AS3: In updated experiments, heater power was measured directly using WEMO smart plugs. This is a more reliable power measurement method than the V^2/R calculation because heater power draw is known to vary slightly in response to controls. Calculated heater power is retained as a cross-check ONLY.
Note on AU3: Equivalent conductance, per series admittance model.
Note on AU4: Open circuit
Note on AU5: Open circuit
Note on AU6: Open circuit
Note on AU7: See 'Resistor Values' spreadsheet
Note on AU8: Open circuit
Note on AU9: See 'Resistor Values' spreadsheet
Note on AU10: See 'Resistor Values' spreadsheet
Note on AU11: Open circuit
Note on AW3: In updated experiments, heater power was measured directly using WEMO smart plugs. This is a more reliable power measurement method than the V^2/R calculation because heater power draw is known to vary slightly in response to controls. Calculated heater power is retained as a cross-check ONLY.
Note on BA3: In updated experiments, heater power was measured directly using WEMO smart plugs. Calculated total output power uses less reliable V^/R power calculations for heaters and is retained as a cross-check ONLY.
Note on BB2: For Scenarios 3-4, independent calculations of converter loss and total system loss are not performed due to the known inaccuracy of V^2/R power calculation for heaters. Use the measured values.
Note on BB14: For Scenarios 3-4, independent calculations of converter loss and total system loss are not performed due to the known inaccuracy of V^2/R power calculation for heaters. Use the measured values.
Note on BI3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html Includes covariances for P=V*I loads
Note on BN3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html Includes covariances for P=V*I loads
Note on BS3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html Includes covariances for P=V*I loads
Note on BX3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html Includes covariances for P=V*I loads
Note on CC3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html Includes covariances for P=V*I loads
Note on CH3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html Includes covariances for P=V*I loads
Note on CJ4: Open circuit
Note on CJ5: Open circuit
Note on CJ6: See 'Resistor Values' spreadsheet
Note on CJ7: Open circuit
Note on CJ8: Open circuit
Note on CJ9: See 'Resistor Values' spreadsheet
Note on CJ10: See 'Resistor Values' spreadsheet
Note on CJ11: See 'Resistor Values' spreadsheet
Note on CL3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html In updated experiments, heater power was measured directly using WEMO smart plugs. This is a more reliable power measurement method than the V^2/R calculation because heater power draw is known to vary slightly in response to controls. Calculated heater power variance is retained as a cross-check ONLY.
Note on CN4: Open circuit
Note on CN5: Open circuit
Note on CN6: See 'Resistor Values' spreadsheet
Note on CN7: Open circuit
Note on CN8: Open circuit
Note on CN9: Open circuit
Note on CN10: Open circuit
Note on CN11: Open circuit
Note on CP3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html In updated experiments, heater power was measured directly using WEMO smart plugs. This is a more reliable power measurement method than the V^2/R calculation because heater power draw is known to vary slightly in response to controls. Calculated heater power variance is retained as a cross-check ONLY.
Note on CR4: Open circuit
Note on CR5: Open circuit
Note on CR6: See 'Resistor Values' spreadsheet
Note on CR7: Open circuit
Note on CR8: Open circuit
Note on CR9: See 'Resistor Values' spreadsheet
Note on CR10: See 'Resistor Values' spreadsheet
Note on CR11: Open circuit
Note on CT3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html In updated experiments, heater power was measured directly using WEMO smart plugs. This is a more reliable power measurement method than the V^2/R calculation because heater power draw is known to vary slightly in response to controls. Calculated heater power variance is retained as a cross-check ONLY.
Note on CV4: Open circuit
Note on CV5: Open circuit
Note on CV6: Open circuit
Note on CV7: See 'Resistor Values' spreadsheet
Note on CV8: Open circuit
Note on CV9: See 'Resistor Values' spreadsheet
Note on CV10: Open circuit
Note on CV11: See 'Resistor Values' spreadsheet
Note on CX3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html In updated experiments, heater power was measured directly using WEMO smart plugs. This is a more reliable power measurement method than the V^2/R calculation because heater power draw is known to vary slightly in response to controls. Calculated heater power variance is retained as a cross-check ONLY.
Note on CZ4: Open circuit
Note on CZ5: Open circuit
Note on CZ6: Open circuit
Note on CZ7: See 'Resistor Values' spreadsheet
Note on CZ8: Open circuit
Note on CZ9: Open circuit
Note on CZ10: See 'Resistor Values' spreadsheet
Note on CZ11: See 'Resistor Values' spreadsheet
Note on DB3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html In updated experiments, heater power was measured directly using WEMO smart plugs. This is a more reliable power measurement method than the V^2/R calculation because heater power draw is known to vary slightly in response to controls. Calculated heater power variance is retained as a cross-check ONLY.
Note on DD4: Open circuit
Note on DD5: Open circuit
Note on DD6: Open circuit
Note on DD7: See 'Resistor Values' spreadsheet
Note on DD8: Open circuit
Note on DD9: See 'Resistor Values' spreadsheet
Note on DD10: See 'Resistor Values' spreadsheet
Note on DD11: Open circuit
Note on DF3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html In updated experiments, heater power was measured directly using WEMO smart plugs. This is a more reliable power measurement method than the V^2/R calculation because heater power draw is known to vary slightly in response to controls. Calculated heater power variance is retained as a cross-check ONLY.
Note on DJ3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html Uses measured variances for ALL loads. (For scenarios 3-4, calculated individual load variances are provided for reference only; measured variances are more trustworthy.) Provided for cross-check ONLY.
Note on DM3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html Uses maximum of calculated or observed variance for P_out. Provided for cross-check ONLY.
Note on DO3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html Uses maximum of calculated or observed variance for P_out. Provided for cross-check ONLY.
Note on DR14: For Scenarios 3-4, independent calculations of converter loss and total system loss are not performed due to the known inaccuracy of V^2/R power calculation for heaters. Use the measured values.
Note on DU1: Calculations follow eq. (7), (8), and (15) from doi:10.1016/j.jcp.2006.03.037. Calculated assuming each run is an independent experiment that yields a single sample with estimate of all relevant quantities (the mean value). Thus, for three runs: n = 3 ν = 3 - 1 = 2 Note this yields much larger confidence intervals than an alternative approach where each 5-second interval is considered a single experiment/sample.
Note on DV3: Note that the sample standard deviation s(ΔP_in) = s(P_in), because the modeled value is fixed. Same for the other confidence interval calculations.

## Scenarios 5-6
Scenarios 5-6: DC (120 VAC Input, 208 VAC Input) | [130 empty] | Model Results |  |  |  |  | Estimates of Error (90% Confidence Interval)
Metadata | Load: Laptop Charger 4 |  |  |  | Load: Laptop Charger 5 |  |  |  | Load: Laptop Charger 6 |  |  |  | Load: LED 1 |  |  |  | Load: LED 2 |  |  |  | Load: LED 3 |  |  |  | Load: Small Resistor 1A |  |  |  | Load: Small Resistor 1B |  |  |  | Load: Small Resistor 1C |  |  |  | Load: Small Resistor 1D |  |  |  | Load: Small Resistor 1E |  |  |  | Load: Small Resistor 1F |  |  |  | Load: Small Resistor 1G |  |  |  | Input | Transformer Secondary | Output |  | Loss | [5 empty] | Load: Laptop Charger 4 |  |  |  |  | Load: Laptop Charger 5 |  |  |  |  | Load: Laptop Charger 6 |  |  |  |  | Load: LED 1 |  |  |  |  | Load: LED 2 |  |  |  |  | Load: LED 3 |  |  |  |  | Load: Small Resistor 1A |  |  |  | Load: Small Resistor 1B |  |  |  | Load: Small Resistor 1C |  |  |  | Load: Small Resistor 1D |  |  |  | Load: Small Resistor 1E |  |  |  | Load: Small Resistor 1F |  |  |  | Load: Small Resistor 1G |  |  |  | Input | Trans. Secondary | Output |  | Loss | [5 empty] | Power Values |  |  |  |  | Input Power: P_in |  |  |  | Transformer Secondary Power: P_sec |  |  |  | Transformer Loss: P_lossTran |  |  |  | Converter Loss: P_lossConv |  |  |  | System Loss: P_loss
Data Set | V_load [V] | I_load [A] | P_load [W] | Calc: P_load [W] | V_load [V] | I_load [A] | P_load [W] | Calc: P_load [W] | V_load [V] | I_load [A] | P_load [W] | Calc: P_load [W] | V_load [V] | I_load [A] | P_load [W] | Calc: P_load [W] | V_load [V] | I_load [A] | P_load [W] | Calc: P_load [W] | V_load [V] | I_load [A] | P_load [W] | Calc: P_load [W] | V_load [V] | R_load [Ω] | P_load [W] | Calc: P_load [W] | V_load [V] | R_load [Ω] | P_load [W] | Calc: P_load [W] | V_load [V] | R_load [Ω] | P_load [W] | Calc: P_load [W] | V_load [V] | R_load [Ω] | P_load [W] | Calc: P_load [W] | V_load [V] | R_load [Ω] | P_load [W] | Calc: P_load [W] | V_load [V] | R_load [Ω] | P_load [W] | Calc: P_load [W] | V_load [V] | R_load [Ω] | P_load [W] | Calc: P_load [W] | P_in [W] | P_sec [W] | P_out [W] | Calc: P_out [W] | P_lossTran [W] | Calc: P_lossTran [W] | P_lossConv [W] | Calc: P_lossConv [W] | P_loss [W] | Calc: P_loss [W] | σ(V_load) [V] | σ(I_load) [A] | COV(V_load,I_load) [(VA)²] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(I_load) [A] | COV(V_load,I_load) [(VA)²] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(I_load) [A] | COV(V_load,I_load) [(VA)²] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(I_load) [A] | COV(V_load,I_load) [(VA)²] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(I_load) [A] | COV(V_load,I_load) [(VA)²] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(I_load) [A] | COV(V_load,I_load) [(VA)²] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(R_load) [Ω] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(R_load) [Ω] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(R_load) [Ω] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(R_load) [Ω] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(R_load) [Ω] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(R_load) [Ω] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(V_load) [V] | σ(R_load) [Ω] | σ(P_load) [W] | Calc: σ(P_load) [W] | σ(P_in) [W] | σ(P_sec) [W] | σ(P_out) [W] | Calc: σ(P_out) [W] | σ(P_lossTran) [W] | Calc: σ(P_lossTran) [W] | σ(P_lossConv) [W] | Calc: σ(P_lossConv) [W] | σ(P_loss) [W] | Calc: σ(P_loss) [W] | P_in [W] | P_sec [W] | P_lossTran [W] | P_lossConv [W] | P_loss [W] | Est. ΔP_in [W] | Conf. ΔP_in [W] | Est. ΔP_in/P_in [%] | Conf. ΔP_in/P_in [%] | Est. ΔP_sec [W] | Conf. ΔP_sec [W] | Est. ΔP_sec/P_sec [%] | Conf. ΔP_sec/P_sec [%] | Est. ΔP_lossTran [W] | Conf. ΔP_lossTran [W] | Est. ΔP_lossTran/P_lossTran [%] | Conf. ΔP_lossTran/P_lossTran [%] | Est. ΔP_lossConv [W] | Conf. ΔP_lossConv [W] | Est. ΔP_lossConv/P_lossConv [%] | Conf. ΔP_lossConv/P_lossConv [%] | Est. ΔP_loss [W] | Conf. ΔP_loss [W] | Est. ΔP_loss/P_loss [%] | Conf. ΔP_loss/P_loss [%]
5.1 | 18.8606 | 0.0066335 | 0.12511 | 0 | 18.7623 | 0.0071469 | 0.13409 | 0 | 18.8401 | 0.012595 | 0.23729 | 0 | 0.24837 | 0 | 3.0673e-06 | 0 | 0.17069 | 0 | 6.3329e-07 | 0 | 0.22113 | 0 | -8.5886e-06 | 0 | 1.9042e-06 |  | 4.2396e-31 | 0 | 1.4144e-06 |  | 2.419e-31 | 0 | 7.9452e-07 |  | 9.0442e-32 | 0 | 5.8666e-07 |  | 5.8342e-32 | 0 | 2.1647e-06 |  | 5.4362e-31 | 0 | 5.4542e-07 |  | 5.4094e-32 | 0 | 3.3976e-07 |  | 3.6473e-32 | 0 | 72.3911 | 19.8386 | 0.49649 | 0 | 52.5525 | 52.5525 | 19.3421 | 19.8386 | 71.8946 | 72.3911 | 0.0054602 | 0.00022444 | -4.2196e-11 | 0.0042697 | 0.00013396 | 0.0064577 | 8.7372e-05 | 3.4238e-07 | 0.0016786 | 0 | 0.0060211 | 8.5598e-05 | 2.3063e-08 | 0.0015863 | 0 | 0.00029432 | 0 | -1.8091e-09 | 2.7621e-07 | 0 | 8.0057e-05 | 0 | -1.8091e-09 | 2.7621e-07 | 0 | 0.00029432 | 0 | -1.8091e-09 | 2.7621e-07 | 0 | 1.0313e-07 |  | 4.2689e-32 | 0 | 1.221e-07 |  | 4.0961e-32 | 0 | 1.4972e-07 |  | 2.4903e-32 | 0 | 6.8975e-08 |  | 7.5585e-33 | 0 | 1.5737e-07 |  | 7.5431e-32 | 0 | 1.7591e-07 |  | 1.872e-32 | 0 | 2.7628e-07 |  | 2.3053e-32 | 0 | 0.049273 | 0.024263 | 0.0055387 | 0.0048543 | 0.027206 | 0.054923 | 0.019617 | 0.024887 | 0.043858 | 0.049583 | 67.9151 | 20.0161 | 47.899 | 19.5201 | 67.4191 | -4.476 | 0.083067 | -6.183% | 0.1147% | 0.17751 | 0.040904 | 0.8948% | 0.2062% | -4.6535 | 0.045866 | -8.855% | 0.08728% | 0.178 | 0.041956 | 0.9203% | 0.2169% | -4.4755 | 0.08359 | -6.225% | 0.1163%
5.2 | 18.5713 | 0.31047 | 5.7659 | 5.7659 | 18.6576 | 0.32632 | 6.0884 | 6.0884 | 18.7633 | 0.36428 | 6.8351 | 6.8351 | 24.3995 | 1.2809 | 31.2542 | 31.2543 | 24.2848 | 1.3036 | 31.6579 | 31.658 | 24.32 | 1.261 | 30.6683 | 30.6684 | 24.3352 | 6.907 | 85.7022 | 85.7394 | 0.00010925 |  | 1.3354e-27 | 0 | 3.1311e-05 |  | 1.1343e-28 | 0 | 1.5634e-05 |  | 2.9278e-29 | 0 | 0.019143 |  | 6.3779e-22 | 0 | -2.6011e-05 |  | 7.6022e-29 | 0 | -0.00011441 |  | 1.4552e-27 | 0 | 294.184 | 239.7017 | 197.9718 | 198.0094 | 54.4824 | 54.4824 | 41.7299 | 41.6923 | 96.2122 | 96.1746 | 0.0070293 | 4.5926e-05 | -2.0392e-05 | 0.0029959 | 0 | 0.0056785 | 0.00057794 | -1.5575e-08 | 0.012122 | 0.010932 | 0.0051339 | 0.0023439 | 3.4791e-08 | 0.044609 | 0.044025 | 0.000828 | 0.013988 | -7.6384e-06 | 0.34025 | 0.3406 | 0.0025394 | 0.012009 | 0.00012358 | 0.28836 | 0.30478 | 0.000828 | 0.013988 | -7.6384e-06 | 0.34025 | 0.3395 | 0.00034004 | 0.045 | 0.0023951 | 0.55861 | 9.9583e-06 |  | 2.3277e-28 | 0 | 7.5195e-06 |  | 4.9432e-29 | 0 | 5.0766e-06 |  | 1.5797e-29 | 0 | 0.033204 |  | 1.1047e-21 | 0 | 2.9236e-06 |  | 1.6039e-29 | 0 | 1.2704e-06 |  | 3.1392e-29 | 0 | 0.90326 | 0.95843 | 0.91964 | 0.79302 | 0.055163 | 1.317 | 0.083546 | 1.3283 | 0.073586 | 1.289 | 283.2921 | 232.9175 | 50.3746 | 35.2675 | 85.6421 | -10.892 | 1.5228 | -3.702% | 0.5176% | -6.7842 | 1.6158 | -2.83% | 0.6741% | -4.1077 | 0.092996 | -7.54% | 0.1707% | -6.4624 | 2.2393 | -15.49% | 5.366% | -10.5701 | 2.1731 | -10.99% | 2.259%
5.3 | 18.3522 | 2.2871 | 41.974 | 41.974 | 18.1838 | 2.2259 | 40.4749 | 40.4749 | 18.4763 | 2.2442 | 41.465 | 41.465 | 24.168 | 1.2463 | 30.1196 | 30.1199 | 24.3144 | 1.2325 | 29.9679 | 29.968 | 24.3118 | 1.2592 | 30.6129 | 30.6131 | 24.2434 | 6.907 | 85.0566 | 85.0935 | 24.2591 | 6.93 | 84.9212 | 84.9212 | 24.2781 | 6.881 | 85.6723 | 85.6599 | 24.2784 | 7.199 | 81.8671 | 81.8784 | -0.00019194 |  | 4.3437e-27 | 0 | -0.00023629 |  | 6.2816e-27 | 0 | -0.00024853 |  | 6.8783e-27 | 0 | 693.0336 | 627.5255 | 552.1314 | 552.1678 | 65.508 | 65.508 | 75.3941 | 75.3577 | 140.9021 | 140.8657 | 0.0021667 | 0.00028418 | -0.00026845 | 0.0051494 | 0 | 0.007411 | 0.0015721 | -2.3574e-07 | 0.044439 | 0.032715 | 0.0047462 | 0.0085908 | 3.2607e-08 | 0.16731 | 0.15909 | 0.013829 | 0.018923 | 5.4157e-05 | 0.44135 | 0.4612 | 0.0019036 | 0.020064 | 7.6542e-05 | 0.48554 | 0.49253 | 0.013829 | 0.018923 | 5.4157e-05 | 0.44135 | 0.46396 | 0.0010724 | 0.045 | 0.0075248 | 0.55445 | 0.00029236 | 0.029 | 0.0020469 | 0.35538 | 0.00026783 | 0.029 | 0.0018902 | 0.36102 | 0.00052503 | 0.049 | 0.0035408 | 0.55732 | 5.1007e-05 |  | 2.3117e-27 | 0 | 2.8893e-05 |  | 1.4369e-27 | 0 | 9.7861e-06 |  | 5.3204e-28 | 0 | 0.59627 | 0.6025 | 1.2202 | 1.2369 | 0.05491 | 0.84767 | 1.7572 | 1.3759 | 1.7294 | 1.3731 | 690.078 | 623.5199 | 66.558 | 71.3879 | 137.946 | -2.9556 | 1.0052 | -0.4265% | 0.145% | -4.0056 | 1.0157 | -0.6383% | 0.1619% | 1.05 | 0.092571 | 1.603% | 0.1413% | -4.0062 | 2.9624 | -5.314% | 3.929% | -2.9562 | 2.9155 | -2.098% | 2.069%
5.4 | 18.1168 | 4.0762 | 73.8475 | 73.8475 | 17.9297 | 3.961 | 71.0194 | 71.0194 | 18.18 | 3.94 | 71.6287 | 71.6287 | 24.0126 | 1.2301 | 29.5375 | 29.5377 | 24.224 | 1.2371 | 29.9669 | 29.9671 | 24.2229 | 1.2383 | 29.9949 | 29.995 | 24.1573 | 6.907 | 84.4539 | 84.4906 | 24.1741 | 6.93 | 84.3274 | 84.3274 | 24.195 | 6.881 | 85.0869 | 85.0745 | 24.1903 | 7.199 | 81.2738 | 81.2851 | 24.1766 | 7.04 | 83.027 | 83.027 | 24.182 | 7.413 | 78.9165 | 78.8845 | 24.1862 | 7.218 | 81.0209 | 81.0433 | 1081.1422 | 992.8758 | 884.1012 | 884.1278 | 88.2664 | 88.2664 | 108.7746 | 108.748 | 197.041 | 197.0144 | 0.0054974 | 0.0014321 | -0.0013184 | 0.047252 | 0 | 0.0014979 | 0.0019626 | -2.8229e-06 | 0.036959 | 0.029538 | 0.0094774 | 0.0014322 | 1.2556e-06 | 0.011356 | 0.047456 | 0.013066 | 0.012059 | 0.00019237 | 0.27355 | 0.30899 | 0.0013055 | 0.015732 | 8.9098e-05 | 0.37949 | 0.38804 | 0.013066 | 0.012059 | 0.00019237 | 0.27355 | 0.31165 | 0.0010628 | 0.045 | 0.0074312 | 0.55052 | 0.00026218 | 0.029 | 0.0018292 | 0.35289 | 0.00031346 | 0.029 | 0.0022047 | 0.35855 | 0.00061527 | 0.049 | 0.0041344 | 0.55328 | 0.00056897 | 0.036 | 0.0039078 | 0.42459 | 0.00030004 | 0.067 | 0.0019583 | 0.71297 | 0.00084834 | 0.037 | 0.0056837 | 0.41547 | 2.5004 | 2.6371 | 1.0105 | 1.4216 | 0.22376 | 3.6341 | 3.6031 | 2.9959 | 3.4481 | 2.8763 | 1095.8613 | 998.4845 | 97.3768 | 114.3825 | 211.7593 | 14.7191 | 4.2153 | 1.361% | 0.3899% | 5.6087 | 4.4458 | 0.5649% | 0.4478% | 9.1104 | 0.37723 | 10.32% | 0.4274% | 5.6079 | 6.0744 | 5.156% | 5.584% | 14.7183 | 5.8131 | 7.47% | 2.95%
6.1 | 18.8713 | 0.005791 | 0.10927 | 0 | 18.7706 | 0.0077878 | 0.14621 | 0 | 18.8233 | 0.016166 | 0.30421 | 0 | 0.17882 | 0 | -5.5029e-06 | 0 | 0.15192 | 0 | -5.4561e-06 | 0 | 0.33221 | 0 | 0.0001376 | 0 | 1.5276e-06 |  | 2.8125e-31 | 0 | 1.1831e-06 |  | 1.7683e-31 | 0 | 7.6449e-07 |  | 8.6251e-32 | 0 | 5.2374e-07 |  | 6.2537e-32 | 0 | 2.4969e-06 |  | 7.1889e-31 | 0 | 5.9785e-07 |  | 6.1397e-32 | 0 | 3.4404e-07 |  | 3.5414e-32 | 0 | 71.9068 | 19.4054 | 0.55982 | 0 | 52.5014 | 52.5014 | 18.8456 | 19.4054 | 71.347 | 71.9068 | 0.024943 | 0.00087469 | 8.1785e-10 | 0.016375 | 0.00044684 | 0.025511 | 0.0017428 | -0.00017775 | 0.032937 | 0 | 0.020265 | 0.0065727 | 0.00011616 | 0.12332 | 0 | 0.00040605 | 0 | 1.8777e-07 | 2.7327e-08 | 0 | 0.00023808 | 0 | 1.8777e-07 | 2.7327e-08 | 0 | 0.00040605 | 0 | 1.8777e-07 | 2.7327e-08 | 0 | 1.8624e-07 |  | 6.5066e-32 | 0 | 1.0648e-07 |  | 2.7978e-32 | 0 | 1.648e-07 |  | 2.6158e-32 | 0 | 3.815e-07 |  | 3.3731e-32 | 0 | 1.6918e-07 |  | 8.8917e-32 | 0 | 1.73e-07 |  | 2.0019e-32 | 0 | 7.5947e-08 |  | 6.8141e-33 | 0 | 0.069555 | 0.024568 | 0.13989 | 0.12869 | 0.045949 | 0.073766 | 0.11532 | 0.14203 | 0.073208 | 0.15622 | 67.9439 | 20.0449 | 47.899 | 19.5229 | 67.4219 | -3.963 | 0.11726 | -5.511% | 0.1631% | 0.63945 | 0.041418 | 3.295% | 0.2134% | -4.6024 | 0.077463 | -8.766% | 0.1475% | 0.67727 | 0.23944 | 3.594% | 1.271% | -3.9252 | 0.26337 | -5.502% | 0.3691%
6.2 | 18.7244 | 0.31663 | 5.9288 | 5.9288 | 18.5076 | 0.32575 | 6.0289 | 6.0289 | 18.7511 | 0.37736 | 7.0759 | 7.0759 | 24.2617 | 1.2568 | 30.4909 | 30.491 | 24.3953 | 1.243 | 30.3231 | 30.3232 | 24.3973 | 1.2536 | 30.5846 | 30.5848 | 24.3247 | 6.907 | 85.6286 | 85.6658 | 8.8024e-05 |  | 8.9802e-28 | 0 | 2.0708e-05 |  | 5.4328e-29 | 0 | 8.6757e-06 |  | 9.6599e-30 | 0 | -1.167e-05 |  | 1.9401e-29 | 0 | -9.7636e-06 |  | 1.1545e-29 | 0 | -0.00011102 |  | 1.3912e-27 | 0 | 290.4821 | 236.6007 | 196.0608 | 196.0984 | 53.8815 | 53.8815 | 40.5399 | 40.5023 | 94.4214 | 94.3837 | 0.0010786 | 0.00035875 | 0.00016775 | 0.0063993 | 0.010132 | 0.0029717 | 0.00023052 | -4.0638e-07 | 0.0032998 | 0.0037734 | 0.0014845 | 0.00029461 | -4.1346e-09 | 0.0059628 | 0.0055473 | 0.0014412 | 0.022117 | -1.1508e-05 | 0.53486 | 0.53595 | 0.0015322 | 0.012867 | -3.4856e-05 | 0.31199 | 0.31051 | 0.0014412 | 0.022117 | -1.1508e-05 | 0.53486 | 0.53895 | 0.0019352 | 0.045 | 0.013624 | 0.55829 | 1.8702e-05 |  | 3.2419e-28 | 0 | 9.0111e-06 |  | 3.545e-29 | 0 | 3.9357e-06 |  | 6.8877e-30 | 0 | 7.2964e-06 |  | 1.5071e-29 | 0 | 2.2859e-06 |  | 5.0043e-30 | 0 | 1.1883e-05 |  | 2.6517e-28 | 0 | 1.5531 | 1.4856 | 1.5679 | 0.99059 | 0.073376 | 2.1492 | 0.091004 | 2.1599 | 0.070658 | 2.2069 | 281.5479 | 231.2105 | 50.3375 | 35.1495 | 85.4869 | -8.9342 | 2.6183 | -3.076% | 0.9014% | -5.3902 | 2.5045 | -2.278% | 1.059% | -3.544 | 0.1237 | -6.577% | 0.2296% | -5.3904 | 3.6413 | -13.3% | 8.982% | -8.9344 | 3.7205 | -9.462% | 3.94%
6.3 | 18.3554 | 2.2872 | 41.9832 | 41.9832 | 18.1771 | 2.2257 | 40.4569 | 40.4569 | 18.4669 | 2.255 | 41.6431 | 41.6431 | 24.0867 | 1.2463 | 30.0201 | 30.0197 | 24.3091 | 1.2556 | 30.5221 | 30.5222 | 24.3108 | 1.271 | 30.8995 | 30.8996 | 24.2453 | 6.907 | 85.0698 | 85.1067 | 24.2596 | 6.93 | 84.9246 | 84.9246 | 24.2786 | 6.881 | 85.6757 | 85.6633 | 24.2792 | 7.199 | 81.8721 | 81.8834 | -0.0001406 |  | 2.291e-27 | 0 | -0.00022087 |  | 5.4638e-27 | 0 | -0.00023687 |  | 6.2577e-27 | 0 | 680.6712 | 619.1576 | 553.0669 | 553.1026 | 61.5136 | 61.5136 | 66.0907 | 66.055 | 127.6043 | 127.5686 | 0.0023396 | 0.00044359 | 0.00011703 | 0.013409 | 0.061739 | 0.0023998 | 0.00016427 | -9.8849e-08 | 0.0024225 | 0.0054264 | 0.0061739 | 0.0043844 | 3.0047e-08 | 0.06721 | 0.082171 | 0.019949 | 0.020779 | 1.2289e-05 | 0.52425 | 0.50185 | 0.00044494 | 0.013506 | 7.6701e-06 | 0.32782 | 0.32904 | 0.019949 | 0.020779 | 1.2289e-05 | 0.52425 | 0.50654 | 0.00021918 | 0.045 | 0.0015381 | 0.55448 | 0.0001583 | 0.029 | 0.0011083 | 0.35539 | 0.00013537 | 0.029 | 0.00095542 | 0.36103 | 0.00052462 | 0.049 | 0.0035381 | 0.55735 | 2.9044e-05 |  | 9.1645e-28 | 0 | 1.5964e-05 |  | 7.2824e-28 | 0 | 8.0201e-06 |  | 3.9878e-28 | 0 | 0.2369 | 0.26203 | 1.3054 | 1.2396 | 0.046333 | 0.35324 | 1.391 | 1.3315 | 1.4137 | 1.3268 | 691.1752 | 624.5539 | 66.6213 | 71.4869 | 138.1082 | 10.504 | 0.39938 | 1.543% | 0.05868% | 5.3963 | 0.44174 | 0.8716% | 0.07134% | 5.1077 | 0.07811 | 8.303% | 0.127% | 5.3962 | 2.345 | 8.165% | 3.548% | 10.5039 | 2.3833 | 8.232% | 1.868%
6.4 | 18.1134 | 4.0727 | 73.7702 | 73.7702 | 17.9434 | 3.9609 | 71.0729 | 71.0729 | 18.1966 | 3.938 | 71.6583 | 71.6583 | 24.0328 | 1.2139 | 29.1744 | 29.1746 | 24.2223 | 1.2148 | 29.4246 | 29.4247 | 24.2247 | 1.2198 | 29.5487 | 29.5488 | 24.1584 | 6.907 | 84.4614 | 84.4981 | 24.1742 | 6.93 | 84.3279 | 84.3279 | 24.1936 | 6.881 | 85.0771 | 85.0648 | 24.1892 | 7.199 | 81.2662 | 81.2774 | 24.1761 | 7.04 | 83.0235 | 83.0235 | 24.1833 | 7.413 | 78.9244 | 78.8925 | 24.1851 | 7.218 | 81.0135 | 81.0359 | 1051.7375 | 975.1903 | 882.7432 | 882.7697 | 76.5472 | 76.5472 | 92.4471 | 92.4206 | 168.9943 | 168.9678 | 0.010102 | 0.0037043 | 0.0014843 | 0.10815 | 0.39133 | 0.0074099 | 0.0021837 | -1.4633e-05 | 0.068536 | 0.017794 | 0.0091766 | 0.014143 | 2.3247e-06 | 0.29172 | 0.26053 | 0.0057428 | 0.022011 | 3.0388e-05 | 0.52251 | 0.5307 | 0.0021333 | 0.023717 | 5.9703e-05 | 0.57191 | 0.57754 | 0.0057428 | 0.022011 | 3.0388e-05 | 0.52251 | 0.53493 | 0.0010064 | 0.045 | 0.0070369 | 0.55056 | 0.00039581 | 0.029 | 0.0027614 | 0.3529 | 0.0001921 | 0.029 | 0.0013511 | 0.35851 | 0.00031754 | 0.049 | 0.0021336 | 0.55322 | 0.00054372 | 0.036 | 0.0037343 | 0.42457 | 0.0012786 | 0.067 | 0.0083456 | 0.71309 | 0.0015275 | 0.037 | 0.010234 | 0.41552 | 1.8226 | 2.3925 | 1.3348 | 1.6426 | 0.57092 | 3.0076 | 3.7051 | 2.9021 | 3.1402 | 2.4536 | 1094.2141 | 996.9917 | 97.2225 | 114.2487 | 211.4711 | 42.4767 | 3.0726 | 4.039% | 0.2921% | 21.8014 | 4.0333 | 2.236% | 0.4136% | 20.6753 | 0.96249 | 27.01% | 1.257% | 21.8016 | 6.2463 | 23.58% | 6.757% | 42.4769 | 5.294 | 25.14% | 3.133%
| 5.1 | 5.2 | 5.3 | 5.4 | 6.1 | 6.2 | 6.3 | 6.4 | [122 empty] | Input
Load: Laptop Charger 4 | 0.12511 | 5.7659 | 41.974 | 73.8475 | 0.10927 | 5.9288 | 41.9832 | 73.7702 | [122 empty] | P_in [W] | P_sec [W] | P_lossTran [W] | P_lossConv [W] | P_loss [W]
Load: Laptop Charger 5 | 0.13409 | 6.0884 | 40.4749 | 71.0194 | 0.14621 | 6.0289 | 40.4569 | 71.0729 | [122 empty] | 72.3911 | 19.8386 | 52.5525 | 19.3421 | 71.8946
Load: Laptop Charger 6 | 0.23729 | 6.8351 | 41.465 | 71.6287 | 0.30421 | 7.0759 | 41.6431 | 71.6583 | [122 empty] | 294.184 | 239.7017 | 54.4824 | 41.7299 | 96.2122
Load: LED 1 | 3.0673e-06 | 31.2542 | 30.1196 | 29.5375 | -5.5029e-06 | 30.4909 | 30.0201 | 29.1744 | [122 empty] | 693.0336 | 627.5255 | 65.508 | 75.3941 | 140.9021
Load: LED 2 | 6.3329e-07 | 31.6579 | 29.9679 | 29.9669 | -5.4561e-06 | 30.3231 | 30.5221 | 29.4246 | [122 empty] | 1081.1422 | 992.8758 | 88.2664 | 108.7746 | 197.041
Load: LED 3 | -8.5886e-06 | 30.6683 | 30.6129 | 29.9949 | 0.0001376 | 30.5846 | 30.8995 | 29.5487 | [122 empty] | 71.9068 | 19.4054 | 52.5014 | 18.8456 | 71.347
Load: Small Resistor 1A | 4.2396e-31 | 85.7022 | 85.0566 | 84.4539 | 2.8125e-31 | 85.6286 | 85.0698 | 84.4614 | [122 empty] | 290.4821 | 236.6007 | 53.8815 | 40.5399 | 94.4214
Load: Small Resistor 1B | 2.419e-31 | 1.3354e-27 | 84.9212 | 84.3274 | 1.7683e-31 | 8.9802e-28 | 84.9246 | 84.3279 | [122 empty] | 680.6712 | 619.1576 | 61.5136 | 66.0907 | 127.6043
Load: Small Resistor 1C | 9.0442e-32 | 1.1343e-28 | 85.6723 | 85.0869 | 8.6251e-32 | 5.4328e-29 | 85.6757 | 85.0771 | [122 empty] | 1051.7375 | 975.1903 | 76.5472 | 92.4471 | 168.9943
Load: Small Resistor 1D | 5.8342e-32 | 2.9278e-29 | 81.8671 | 81.2738 | 6.2537e-32 | 9.6599e-30 | 81.8721 | 81.2662
Load: Small Resistor 1E | 5.4362e-31 | 6.3779e-22 | 4.3437e-27 | 83.027 | 7.1889e-31 | 1.9401e-29 | 2.291e-27 | 83.0235
Load: Small Resistor 1F | 5.4094e-32 | 7.6022e-29 | 6.2816e-27 | 78.9165 | 6.1397e-32 | 1.1545e-29 | 5.4638e-27 | 78.9244
Load: Small Resistor 1G | 3.6473e-32 | 1.4552e-27 | 6.8783e-27 | 81.0209 | 3.5414e-32 | 1.3912e-27 | 6.2577e-27 | 81.0135
Output power (Calc) | 0.49649 | 197.9718 | 552.1314 | 884.1012 | 0.55982 | 196.0608 | 553.0669 | 882.7432
Check Output Power | 0.49649 | 197.9718 | 552.1314 | 884.1012 | 0.55982 | 196.0608 | 553.0669 | 882.7432
Resistor total power (+ LEDs) | -4.888e-06 | 179.2825 | 428.2175 | 667.6056 | 0.00012664 | 177.0272 | 428.9838 | 666.2417
Note on E4: Setting to zero
Note on E8: Setting to zero
Note on I4: Setting to zero
Note on I8: Setting to zero
Note on M4: Setting to zero
Note on M8: Setting to zero
Note on AA4: Open circuit
Note on AA5: Small Resistor 1A See 'Resistor Values' spreadsheet
Note on AA6: Small Resistor 1A See 'Resistor Values' spreadsheet
Note on AA7: Small Resistor 1A See 'Resistor Values' spreadsheet
Note on AA8: Open circuit
Note on AA9: Small Resistor 1A See 'Resistor Values' spreadsheet
Note on AA10: Small Resistor 1A See 'Resistor Values' spreadsheet
Note on AA11: Small Resistor 1A See 'Resistor Values' spreadsheet
Note on AE4: Open circuit
Note on AE5: Open circuit
Note on AE6: Small Resistor 1B See 'Resistor Values' spreadsheet
Note on AE7: Small Resistor 1B See 'Resistor Values' spreadsheet
Note on AE8: Open circuit
Note on AE9: Open circuit
Note on AE10: Small Resistor 1B See 'Resistor Values' spreadsheet
Note on AE11: Small Resistor 1B See 'Resistor Values' spreadsheet
Note on AI4: Open circuit
Note on AI5: Open circuit
Note on AI6: Small Resistor 1C See 'Resistor Values' spreadsheet
Note on AI7: Small Resistor 1C See 'Resistor Values' spreadsheet
Note on AI8: Open circuit
Note on AI9: Open circuit
Note on AI10: Small Resistor 1C See 'Resistor Values' spreadsheet
Note on AI11: Small Resistor 1C See 'Resistor Values' spreadsheet
Note on AM4: Open circuit
Note on AM5: Open circuit
Note on AM6: Small Resistor 1D See 'Resistor Values' spreadsheet
Note on AM7: Small Resistor 1D See 'Resistor Values' spreadsheet
Note on AM8: Open circuit
Note on AM9: Open circuit
Note on AM10: Small Resistor 1D See 'Resistor Values' spreadsheet
Note on AM11: Small Resistor 1D See 'Resistor Values' spreadsheet
Note on AQ4: Open circuit
Note on AQ5: Open circuit
Note on AQ6: Open circuit
Note on AQ7: Small Resistor 1E See 'Resistor Values' spreadsheet
Note on AQ8: Open circuit
Note on AQ9: Small Resistor 1A See 'Resistor Values' spreadsheet
Note on AQ10: Open circuit
Note on AQ11: Small Resistor 1E See 'Resistor Values' spreadsheet
Note on AU4: Open circuit
Note on AU5: Open circuit
Note on AU6: Open circuit
Note on AU7: Small Resistor 1F See 'Resistor Values' spreadsheet
Note on AU8: Open circuit
Note on AU9: Small Resistor 1A See 'Resistor Values' spreadsheet
Note on AU10: Open circuit
Note on AU11: Small Resistor 1F See 'Resistor Values' spreadsheet
Note on AY4: Open circuit
Note on AY5: Open circuit
Note on AY6: Open circuit
Note on AY7: Small Resistor 1G See 'Resistor Values' spreadsheet
Note on AY8: Open circuit
Note on AY9: Small Resistor 1A See 'Resistor Values' spreadsheet
Note on AY10: Open circuit
Note on AY11: Small Resistor 1G See 'Resistor Values' spreadsheet
Note on BP3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html Includes covariances for P=V*I loads
Note on BP5: SQRT argument is a small negative number, yielding NaN. Rounding off to zero with MAX function to allow the calculation to work. -Stephen Frank This is true for data sets 5.2, 5.3, 5.4 -Stephen Frank
Note on BU3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html Includes covariances for P=V*I loads
Note on BZ3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html Includes covariances for P=V*I loads
Note on CB4: Open Circuit
Note on CB8: Open Circuit
Note on CE3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html Includes covariances for P=V*I loads
Note on CG4: Open Circuit
Note on CG8: Open Circuit
Note on CJ3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html Includes covariances for P=V*I loads
Note on CL4: Open Circuit
Note on CL8: Open Circuit
Note on CO3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html Includes covariances for P=V*I loads
Note on CQ4: Open circuit
Note on CQ5: Small Resistor 1A See 'Resistor Values' spreadsheet
Note on CQ6: Small Resistor 1A See 'Resistor Values' spreadsheet
Note on CQ7: Small Resistor 1A See 'Resistor Values' spreadsheet
Note on CQ8: Open circuit
Note on CQ9: Small Resistor 1A See 'Resistor Values' spreadsheet
Note on CQ10: Small Resistor 1A See 'Resistor Values' spreadsheet
Note on CQ11: Small Resistor 1A See 'Resistor Values' spreadsheet
Note on CS3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html
Note on CU4: Open circuit
Note on CU5: Open circuit
Note on CU6: Small Resistor 1B See 'Resistor Values' spreadsheet
Note on CU7: Small Resistor 1B See 'Resistor Values' spreadsheet
Note on CU8: Open circuit
Note on CU9: Open circuit
Note on CU10: Small Resistor 1B See 'Resistor Values' spreadsheet
Note on CU11: Small Resistor 1B See 'Resistor Values' spreadsheet
Note on CW3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html
Note on CY4: Open circuit
Note on CY5: Open circuit
Note on CY6: Small Resistor 1C See 'Resistor Values' spreadsheet
Note on CY7: Small Resistor 1C See 'Resistor Values' spreadsheet
Note on CY8: Open circuit
Note on CY9: Open circuit
Note on CY10: Small Resistor 1C See 'Resistor Values' spreadsheet
Note on CY11: Small Resistor 1C See 'Resistor Values' spreadsheet
Note on DA3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html
Note on DC4: Open circuit
Note on DC5: Open circuit
Note on DC6: Small Resistor 1D See 'Resistor Values' spreadsheet
Note on DC7: Small Resistor 1D See 'Resistor Values' spreadsheet
Note on DC8: Open circuit
Note on DC9: Open circuit
Note on DC10: Small Resistor 1D See 'Resistor Values' spreadsheet
Note on DC11: Small Resistor 1D See 'Resistor Values' spreadsheet
Note on DE3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html
Note on DG4: Open circuit
Note on DG5: Open circuit
Note on DG6: Open circuit
Note on DG7: Small Resistor 1E See 'Resistor Values' spreadsheet
Note on DG8: Open circuit
Note on DG9: Open circuit
Note on DG10: Open circuit
Note on DG11: Small Resistor 1E See 'Resistor Values' spreadsheet
Note on DI3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html
Note on DK4: Open circuit
Note on DK5: Open circuit
Note on DK6: Open circuit
Note on DK7: Small Resistor 1F See 'Resistor Values' spreadsheet
Note on DK8: Open circuit
Note on DK9: Open circuit
Note on DK10: Open circuit
Note on DK11: Small Resistor 1F See 'Resistor Values' spreadsheet
Note on DM3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html
Note on DO4: Open circuit
Note on DO5: Open circuit
Note on DO6: Open circuit
Note on DO7: Small Resistor 1G See 'Resistor Values' spreadsheet
Note on DO8: Open circuit
Note on DO9: Open circuit
Note on DO10: Open circuit
Note on DO11: Small Resistor 1G See 'Resistor Values' spreadsheet
Note on DQ3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html
Note on DU3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html Uses measured variances for V*I loads, calculated variances for V²/R loads. Uses maximum of calculated or observed variance for P_out. Use instead of "measured" value in order to account for uncertainty in small load resistance.
Note on DW3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html Provided for cross-check ONLY.
Note on DY3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html Uses maximum of calculated or observed variance for P_out. Use instead of "measured" value in order to account for uncertainty in small load resistance.
Note on EA3: Ref: https://mathworld.wolfram.com/ErrorPropagation.html Uses maximum of calculated or observed variance for P_out. Use instead of "measured" value in order to account for uncertainty in small load resistance.
Note on EG1: Calculations follow eq. (7), (8), and (15) from doi:10.1016/j.jcp.2006.03.037. Calculated assuming each run is an independent experiment that yields a single sample with estimate of all relevant quantities (the mean value). Thus, for three runs: n = 3 ν = 3 - 1 = 2 Note this yields much larger confidence intervals than an alternative approach where each 5-second interval is considered a single experiment/sample.
Note on EH3: Note that the sample standard deviation s(ΔP_in) = s(P_in), because the modeled value is fixed. Same for the other confidence interval calculations.
Note on ET3: Uses the maximum of "measured" variance or independently estimated variance.
Note on EX3: Uses the maximum of "measured" variance or independently estimated variance.

## Data Scenarios 1-2
Scenario | Data Set | Run | Summary | P_In | P_Secondary | P_Out | P_TransformerLoss | P_ConverterLoss | P_SystemLoss | V_A | V_A_deg | V_AB | V_AB_deg | V_B | V_B_deg | V_BC | V_BC_deg | V_C | V_C_deg | V_CA | V_CA_deg | I_A | I_A_deg | I_B | I_B_deg | I_C | I_C_deg | Delta->Wye P_A | Delta->Wye P_B | Delta->Wye P_C | V_an | V_an_deg | V_bn | V_bn_deg | V_cn | V_cn_deg | I_a | I_an_deg | I_b | I_bn_deg | I_c | I_cn_deg | P_a | P_b | P_c | V_OUT_PS1 | V_OUT_PS2 | V_OUT_PS3 | P_OUT_PS1 | P_OUT_PS2 | P_OUT_PS3 | V_LED_1 | V_LED_2 | V_LED_3 | I_LED_1 | I_LED_2 | I_LED_3 | P_LED_1 | P_LED_2 | P_LED_3 | V_LAPTOP_3_OUTPUT | V_LAPTOP_4_OUTPUT | V_LAPTOP_5_OUTPUT | I_LAPTOP_3_OUTPUT | I_LAPTOP_4_OUTPUT | I_LAPTOP_5_OUTPUT | P_LAPTOP_3_OUTPUT | P_LAPTOP_4_OUTPUT | P_LAPTOP_5_OUTPUT | V_LED_1 * I_LED_1 | V_LED_2 * I_LED_2 | V_LED_3 * I_LED_3 | V_LAPTOP_3_OUTPUT * I_LAPTOP_3_OUTPUT | V_LAPTOP_4_OUTPUT * I_LAPTOP_4_OUTPUT | V_LAPTOP_5_OUTPUT * I_LAPTOP_5_OUTPUT
1 | 1.1 | 1.1.1 | Variance | 0.0032048 | 0.0032147 | 0.00010277 | 0.0020679 | 0.0039556 | 0.0040106 | 0.030784 | 1.3171e-29 | 0.056982 | 0 | 0.010124 | 0 | 0.027472 | 2.1073e-28 | 0.01233 | 0 | 0.075298 | 0 | 1.8772e-07 | 0.00030578 | 1.1063e-07 | 0.0027911 | 6.1871e-08 | 0.00064684 | 0.0013199 | 0.001578 | 0.00042299 | 0.0036279 | 1.2266e-37 | 0.0047802 | 0 | 0.0017562 | 2.6341e-29 | 7.2456e-09 | 0.0017655 | 2.3541e-07 | 0.004392 | 3.475e-07 | 0.00091726 | 0.00014485 | 0.00049997 | 0.00065688 | 3.312e-08 | 1.3578e-07 | 5.4557e-08 | 3.7987e-42 | 1.5811e-41 | 6.2582e-42 | 2.5915e-07 | 2.3027e-07 | 3.6902e-07 | 5.6697e-08 | 5.2254e-08 | 1.5046e-08 | 3.3468e-05 | 3.0569e-05 | 8.7917e-06 | 7.5626e-08 | 9.9287e-08 | 7.9688e-09 | 5.6628e-09 | 6.8343e-09 | 2.2549e-08 | 2.0363e-06 | 2.3666e-06 | 7.8854e-06
1 | 1.1 | 1.1.2 | Variance | 0.0027582 | 0.00064521 | 8.6194e-05 | 0.0018443 | 0.00066697 | 0.0024515 | 0.012241 | 1.6463e-29 | 0.037306 | 0 | 0.011357 | 0 | 0.033155 | 1.7561e-28 | 0.011282 | 0 | 0.034183 | 0 | 7.0404e-08 | 0.0001271 | 8.7964e-08 | 0.0005598 | 5.1118e-08 | 0.00036262 | 0.00092596 | 0.00046378 | 0.00016263 | 0.0023871 | 4.0887e-38 | 0.0021753 | 0 | 0.0021155 | 7.0243e-29 | 1.0119e-08 | 0.00052101 | 3.6286e-07 | 0.0090624 | 4.2998e-07 | 0.0023458 | 5.2088e-05 | 0.00011028 | 0.00014901 | 6.1504e-08 | 1.0453e-07 | 3.1095e-08 | 7.054e-42 | 1.2171e-41 | 3.5667e-42 | 4.1449e-07 | 5.8129e-07 | 1.1988e-06 | 2.5623e-08 | 2.4931e-08 | 2.9534e-08 | 1.5095e-05 | 1.4603e-05 | 1.7299e-05 | 1.3211e-07 | 5.5735e-08 | 1.0221e-08 | 2.7875e-09 | 1.1677e-08 | 2.8754e-08 | 1.0036e-06 | 4.0429e-06 | 1.0062e-05
1 | 1.1 | 1.1.3 | Variance | 0.0023392 | 0.00036386 | 5.5273e-05 | 0.0018951 | 0.00040806 | 0.0024777 | 0.011279 | 1.6463e-29 | 0.032153 | 0 | 0.013422 | 0 | 0.036604 | 7.0243e-29 | 0.0091879 | 0 | 0.032945 | 0 | 9.4914e-08 | 0.00014617 | 1.6673e-07 | 0.00078134 | 7.1211e-08 | 0.0010976 | 0.00098497 | 0.0013852 | 0.00049158 | 0.002032 | 2.2488e-38 | 0.0020841 | 0 | 0.002319 | 5.2682e-29 | 8.2801e-09 | 0.00037461 | 3.286e-07 | 0.0062491 | 2.7037e-07 | 0.00096804 | 4.0108e-05 | 9.0283e-05 | 0.0001158 | 6.3422e-09 | 3.2744e-08 | 3.3174e-08 | 7.2739e-43 | 3.8121e-42 | 3.805e-42 | 3.8253e-07 | 5.1925e-07 | 9.989e-07 | 2.8243e-08 | 6.9292e-08 | 1.7798e-08 | 1.6575e-05 | 4.0708e-05 | 1.0358e-05 | 1.1394e-07 | 4.9268e-08 | 2.1624e-09 | 9.788e-09 | 3.4399e-09 | 2.0292e-08 | 3.5231e-06 | 1.1907e-06 | 7.0987e-06
1 | 1.2 | 1.2.1 | Variance | 0.16503 | 0.15291 | 0.17492 | 0.0033349 | 0.0049864 | 0.0070918 | 0.01479 | 1.4817e-29 | 0.040844 | 0 | 0.013539 | 0 | 0.042917 | 1.7561e-28 | 0.015663 | 0 | 0.048239 | 0 | 1.75e-06 | 0.020028 | 2.21e-06 | 0.025425 | 2.5473e-06 | 0.01362 | 0.037763 | 0.0086215 | 0.027777 | 0.0025567 | 3.6844e-34 | 0.0030135 | 0 | 0.0026905 | 2.1073e-28 | 1.2018e-06 | 0.0008426 | 4.5428e-06 | 0.0018482 | 1.139e-05 | 0.0055334 | 0.013235 | 0.045955 | 0.0043307 | 7.6587e-08 | 6.6167e-06 | 1.1629e-07 | 8.7846e-42 | 7.7116e-40 | 1.3341e-41 | 2.076e-06 | 2.6491e-06 | 2.1675e-06 | 3.2491e-05 | 3.0846e-05 | 2.8178e-05 | 0.018516 | 0.017378 | 0.015954 | 2.6114e-06 | 2.9449e-06 | 6.0262e-06 | 9.4056e-07 | 2.9089e-05 | 2.7778e-06 | 0.00056392 | 0.0084376 | 0.0015411
1 | 1.2 | 1.2.2 | Variance | 0.024525 | 0.019149 | 0.02062 | 0.0021522 | 0.0019036 | 0.0025394 | 0.012508 | 1.3171e-29 | 0.037268 | 0 | 0.01445 | 0 | 0.048374 | 1.0536e-28 | 0.015094 | 0 | 0.040525 | 0 | 6.5358e-07 | 0.0084716 | 6.7559e-07 | 0.011085 | 1.0141e-06 | 0.0079246 | 0.0054441 | 0.005592 | 0.0025982 | 0.0023969 | 2.0097e-34 | 0.0025926 | 0 | 0.0031029 | 2.1073e-28 | 1.9718e-06 | 0.0006364 | 2.188e-06 | 0.00091857 | 2.6565e-06 | 0.0023207 | 0.0023946 | 0.0040006 | 0.0039255 | 3.119e-08 | 1.3906e-06 | 1.0994e-07 | 3.5773e-42 | 1.6198e-40 | 1.2612e-41 | 1.3199e-06 | 1.6093e-06 | 2.4084e-06 | 7.3758e-06 | 8.2774e-06 | 4.5766e-06 | 0.0041297 | 0.0045908 | 0.0024784 | 6.6355e-06 | 8.2351e-09 | 2.0177e-07 | 5.8329e-07 | 9.7527e-08 | 7.5946e-06 | 0.00055059 | 3.3417e-05 | 0.0023815
1 | 1.2 | 1.2.3 | Variance | 0.012233 | 0.011982 | 0.01251 | 0.001346 | 0.00086153 | 0.0027507 | 0.0035852 | 1.6463e-29 | 0.01032 | 0 | 0.0059168 | 0 | 0.042099 | 7.0243e-29 | 0.014339 | 0 | 0.019081 | 0 | 4.4391e-07 | 0.002013 | 2.2894e-07 | 0.0014434 | 3.2207e-07 | 0.00080076 | 0.0052257 | 0.0022809 | 0.0037328 | 0.00065919 | 5.0242e-34 | 0.0012227 | 0 | 0.0026942 | 2.1073e-28 | 4.7218e-06 | 0.0018642 | 3.3518e-06 | 0.0011307 | 6.2405e-06 | 0.00095587 | 0.00059014 | 0.00096275 | 0.0058609 | 1.3482e-08 | 4.5717e-07 | 2.1528e-08 | 1.5463e-42 | 5.3241e-41 | 2.4696e-42 | 9.2632e-07 | 1.1344e-06 | 2.6072e-06 | 3.2497e-06 | 2.1893e-06 | 8.5259e-07 | 0.0017982 | 0.0011827 | 0.00042466 | 8.1906e-07 | 4.5958e-08 | 4.2696e-07 | 2.4935e-07 | 1.9824e-07 | 1.3619e-05 | 0.00014167 | 6.2904e-05 | 0.0042168
1 | 1.3 | 1.3.1 | Variance | 0.052182 | 0.068066 | 0.10708 | 0.0033117 | 0.0079454 | 0.016854 | 0.0069715 | 1.3171e-29 | 0.019472 | 0 | 0.0059913 | 0 | 0.01744 | 6.1463e-29 | 0.0062099 | 0 | 0.020608 | 0 | 4.0506e-07 | 0.00062176 | 4.4925e-07 | 0.00032604 | 4.1143e-07 | 0.00041687 | 0.014618 | 0.0056922 | 0.0064899 | 0.0012491 | 1.8757e-33 | 0.0013475 | 0 | 0.0012327 | 2.1073e-28 | 2.9135e-06 | 0.00051368 | 4.0441e-06 | 0.00042241 | 9.9058e-06 | 0.0003044 | 0.0087204 | 0.020432 | 0.021403 | 4.1089e-08 | 1.0932e-07 | 3.0467e-07 | 3.7866e-06 | 9.9502e-06 | 2.9429e-05 | 1.8266e-06 | 2.2287e-06 | 1.9376e-06 | 2.953e-05 | 2.516e-05 | 1.8636e-05 | 0.016829 | 0.01417 | 0.010502 | 9.6204e-07 | 1.2647e-06 | 1.0045e-05 | 1.0908e-06 | 4.9767e-05 | 3.3077e-06 | 0.00050993 | 0.015648 | 0.002015
1 | 1.3 | 1.3.2 | Variance | 0.19861 | 0.14432 | 0.16119 | 0.012896 | 0.026802 | 0.051135 | 0.10332 | 1.4817e-29 | 0.30415 | 0 | 0.10494 | 0 | 0.33556 | 1.7561e-28 | 0.1152 | 0 | 0.33076 | 0 | 1.1858e-06 | 0.0048251 | 7.4495e-07 | 0.0057994 | 1.0275e-06 | 0.0050393 | 0.027837 | 0.031338 | 0.025488 | 0.01949 | 6.6989e-34 | 0.021278 | 0 | 0.021358 | 2.1073e-28 | 8.2891e-06 | 0.0013919 | 1.6284e-05 | 0.00086789 | 1.2189e-05 | 0.0010242 | 0.019197 | 0.033208 | 0.018989 | 1.48e-08 | 1.7334e-07 | 6.8837e-08 | 1.3639e-06 | 1.5775e-05 | 6.6491e-06 | 2.0286e-06 | 2.4604e-06 | 2.0954e-06 | 2.2945e-05 | 2.6446e-05 | 2.1064e-05 | 0.013015 | 0.014884 | 0.011882 | 1.8678e-07 | 1.1618e-06 | 3.6397e-06 | 8.3006e-07 | 7.9762e-05 | 2.0417e-06 | 0.00032137 | 0.025215 | 0.0010638
1 | 1.3 | 1.3.3 | Variance | 0.78698 | 0.63015 | 0.066925 | 0.0096805 | 0.46899 | 0.60371 | 0.01063 | 1.4817e-29 | 0.022384 | 0 | 0.0063005 | 0 | 0.025251 | 2.1073e-28 | 0.01235 | 0 | 0.040215 | 0 | 3.2962e-06 | 0.00074033 | 5.6859e-07 | 0.0011923 | 1.895e-06 | 0.0023162 | 0.15813 | 0.007419 | 0.21391 | 0.0014611 | 6.6989e-34 | 0.0024543 | 0 | 0.0014877 | 2.1073e-28 | 2.0363e-06 | 0.0014881 | 5.3305e-05 | 0.0011009 | 8.427e-06 | 0.0012187 | 0.039416 | 0.4319 | 0.0094796 | 9.1846e-09 | 8.8728e-08 | 1.1377e-07 | 8.4641e-07 | 8.0751e-06 | 1.0989e-05 | 1.7175e-06 | 2.1504e-06 | 2.2627e-06 | 1.2097e-05 | 1.9802e-05 | 1.8004e-05 | 0.0068108 | 0.01111 | 0.010113 | 1.5576e-06 | 9.3175e-07 | 4.4778e-06 | 1.2582e-06 | 2.1983e-05 | 2.2506e-06 | 0.00063765 | 0.0069847 | 0.0011392
1 | 1.4 | 1.4.1 | Variance | 0.84541 | 0.51076 | 0.099934 | 0.053273 | 0.24937 | 0.44569 | 0.0085502 | 1.6463e-29 | 0.022917 | 0 | 0.0080656 | 0 | 0.027334 | 2.1073e-28 | 0.010684 | 0 | 0.031656 | 0 | 2.5389e-06 | 0.00099869 | 1.1643e-06 | 0.0027618 | 1.2632e-06 | 0.0037989 | 0.11752 | 0.063855 | 0.20725 | 0.0014609 | 2.1436e-33 | 0.0021083 | 0 | 0.0018656 | 2.1073e-28 | 4.1313e-06 | 0.00043678 | 5.0127e-05 | 0.00065112 | 1.0134e-05 | 0.0017301 | 0.062244 | 0.38144 | 0.04752 | 6.5442e-08 | 3.6764e-07 | 1.0195e-07 | 1.9108e-05 | 0.0001055 | 3.021e-05 | 2.2103e-06 | 2.5791e-06 | 2.6553e-06 | 1.6583e-05 | 2.157e-05 | 1.8495e-05 | 0.0093472 | 0.012093 | 0.010369 | 1.0018e-06 | 9.7988e-07 | 1.8734e-06 | 4.2816e-07 | 1.8567e-05 | 3.1527e-06 | 0.00023917 | 0.0056402 | 0.0010766
1 | 1.4 | 1.4.2 | Variance | 2.5877 | 2.1956 | 0.092627 | 0.019278 | 1.4527 | 1.7729 | 0.012946 | 1.3171e-29 | 0.042983 | 0 | 0.01394 | 0 | 0.042739 | 3.5121e-29 | 0.012205 | 0 | 0.031553 | 0 | 9.3792e-06 | 0.00089583 | 1.2447e-06 | 0.0011277 | 3.8827e-06 | 0.0022524 | 0.34753 | 0.12087 | 0.48621 | 0.0029046 | 1.7417e-33 | 0.0021318 | 0 | 0.002873 | 2.1073e-28 | 2.7216e-05 | 0.0024492 | 0.00013854 | 0.0004645 | 8.4709e-06 | 0.00078006 | 0.096086 | 0.95919 | 0.051029 | 8.6234e-07 | 1.2079e-06 | 6.1134e-08 | 0.00025178 | 0.00034665 | 1.8115e-05 | 2.0634e-06 | 2.5027e-06 | 2.8287e-06 | 1.718e-05 | 1.9107e-05 | 1.3032e-05 | 0.0097066 | 0.010695 | 0.0072445 | 3.3077e-06 | 2.3386e-06 | 4.2873e-06 | 5.0154e-07 | 3.247e-05 | 4.7582e-06 | 0.00038117 | 0.0096901 | 0.0022205
1 | 1.4 | 1.4.3 | Variance | 0.16253 | 0.16924 | 0.031315 | 0.010678 | 0.27253 | 0.23781 | 0.012327 | 2.1951e-29 | 0.042889 | 0 | 0.013834 | 0 | 0.03852 | 1.0536e-28 | 0.013999 | 0 | 0.039091 | 0 | 2.6666e-06 | 0.0022318 | 1.8319e-06 | 0.00056994 | 3.7086e-06 | 0.00045863 | 0.078977 | 0.045466 | 0.092019 | 0.0028587 | 3.2155e-33 | 0.0024739 | 0 | 0.0023758 | 2.1073e-28 | 2.1029e-05 | 0.00045379 | 9.0602e-05 | 0.0001573 | 1.6118e-05 | 0.00050523 | 0.090603 | 0.50467 | 0.0044602 | 8.1377e-09 | 4.5093e-07 | 8.2171e-08 | 2.3761e-06 | 0.00012941 | 2.4351e-05 | 2.0373e-06 | 2.4455e-06 | 2.8191e-06 | 2.4304e-05 | 1.9075e-05 | 1.3936e-05 | 0.013791 | 0.010675 | 0.0077601 | 3.5694e-06 | 1.1847e-07 | 2.1625e-06 | 4.262e-07 | 4.068e-05 | 3.21e-06 | 0.00031995 | 0.013439 | 0.0014161
2 | 2.1 | 2.1.1 | Variance | 0.0033264 | 0.0013846 | 6.5788e-05 | 0.00174 | 0.0016101 | 0.0035037 | 0.017041 | 2.1951e-29 | 0.032382 | 0 | 0.0097273 | 0 | 0.025486 | 2.1073e-28 | 0.0089289 | 0 | 0.049253 | 0 | 1.2603e-07 | 0.00014355 | 1.2913e-07 | 0.0012095 | 6.512e-08 | 0.00048661 | 0.0012491 | 0.00091325 | 0.00028843 | 0.0020568 | 4.702e-38 | 0.0031317 | 0 | 0.0016006 | 2.1073e-28 | 5.0263e-09 | 0.00040751 | 4.0704e-07 | 0.0049779 | 4.5435e-07 | 0.0017263 | 4.6272e-05 | 0.00023662 | 0.00036454 | 8.9945e-09 | 2.4928e-08 | 2.2444e-08 | 1.0316e-42 | 2.902e-42 | 2.5742e-42 | 3.3463e-07 | 2.3899e-07 | 6.2748e-07 | 3.557e-08 | 3.2375e-08 | 2.947e-08 | 2.091e-05 | 1.8959e-05 | 1.7368e-05 | 7.7987e-08 | 3.9469e-08 | 2.3871e-09 | 6.8314e-09 | 5.9154e-09 | 3.0727e-08 | 2.458e-06 | 2.0481e-06 | 1.0747e-05
2 | 2.1 | 2.1.2 | Variance | 0.0017973 | 0.00044205 | 0.0001065 | 0.0013064 | 0.00053632 | 0.0021173 | 0.011428 | 1.7561e-29 | 0.026543 | 0 | 0.0091809 | 0 | 0.031517 | 7.9023e-29 | 0.009817 | 0 | 0.03322 | 0 | 1.1579e-07 | 0.00033285 | 1.2663e-07 | 0.0010513 | 8.9328e-08 | 0.00045719 | 0.00080508 | 0.00076418 | 0.00012075 | 0.0016615 | 2.2488e-38 | 0.0020905 | 3.5121e-29 | 0.0019854 | 1.4049e-28 | 5.4895e-09 | 0.00047889 | 4.7686e-08 | 0.00097293 | 7.5753e-08 | 0.00027704 | 0.00011147 | 5.3095e-05 | 0.00012621 | 5.1146e-09 | 1.2822e-08 | 1.1621e-07 | 5.866e-43 | 1.4927e-42 | 1.3328e-41 | 2.4792e-07 | 1.7115e-07 | 4.6771e-07 | 4.1454e-08 | 4.8544e-08 | 2.5373e-08 | 2.433e-05 | 2.84e-05 | 1.4895e-05 | 5.9016e-08 | 2.7674e-08 | 6.6723e-09 | 4.2167e-09 | 1.1753e-08 | 1.2934e-08 | 1.5177e-06 | 4.0666e-06 | 4.5245e-06
2 | 2.1 | 2.1.3 | Variance | 0.001966 | 0.00049477 | 5.2838e-05 | 0.0011373 | 0.00055435 | 0.0019342 | 0.0074412 | 1.3171e-29 | 0.024 | 0 | 0.0081826 | 3.5121e-29 | 0.023191 | 2.1073e-28 | 0.0063964 | 0 | 0.018875 | 0 | 1.3783e-07 | 0.00015272 | 1.379e-07 | 0.0010584 | 8.2838e-08 | 0.00036401 | 0.0010313 | 0.00042955 | 0.00011516 | 0.0015115 | 8.1774e-39 | 0.0011903 | 0 | 0.0014624 | 1.7561e-29 | 7.0609e-09 | 0.00033973 | 2.9518e-07 | 0.0057994 | 2.731e-07 | 0.0010584 | 3.3592e-05 | 8.5396e-05 | 0.00016519 | 5.4927e-09 | 6.4504e-07 | 1.4512e-08 | 6.2996e-43 | 7.5094e-41 | 1.6643e-42 | 4.1277e-08 | 1.3336e-07 | 2.6523e-07 | 1.8143e-08 | 3.2194e-08 | 1.8758e-08 | 1.0673e-05 | 1.887e-05 | 1.0945e-05 | 3.9784e-08 | 2.3345e-08 | 9.4617e-09 | 9.4219e-09 | 5.3704e-09 | 1.071e-08 | 3.3921e-06 | 1.8588e-06 | 3.7461e-06
2 | 2.2 | 2.2.1 | Variance | 0.31427 | 0.12223 | 0.46888 | 0.057511 | 1.0456 | 1.501 | 0.023864 | 1.3171e-29 | 0.069392 | 0 | 0.026754 | 0 | 0.095195 | 2.1073e-28 | 0.032367 | 0 | 0.084402 | 0 | 1.6554e-06 | 0.00016404 | 7.2576e-06 | 0.0003512 | 8.0207e-06 | 0.00061477 | 0.022671 | 0.039103 | 0.10189 | 0.0042812 | 4.4213e-33 | 0.0052266 | 0 | 0.0078804 | 1.7561e-28 | 1.3807e-05 | 0.0032777 | 7.4101e-06 | 0.0039036 | 0.0001368 | 0.00064877 | 0.065206 | 0.021102 | 0.065436 | 5.8128e-09 | 2.6735e-07 | 7.8352e-08 | 3.3734e-06 | 3.1123e-41 | 4.2274e-05 | 6.1026e-06 | 6.6308e-06 | 8.3689e-06 | 9.3051e-05 | 8.1522e-05 | 0.00011929 | 0.05319 | 0.046156 | 0.068039 | 1.1739e-06 | 5.8751e-07 | 8.0548e-06 | 4.8187e-07 | 2.196e-06 | 1.8784e-06 | 0.00019243 | 0.00071506 | 0.00085469
2 | 2.2 | 2.2.2 | Variance | 0.10856 | 0.18023 | 0.12603 | 0.049996 | 0.50785 | 0.30145 | 0.0067207 | 1.3171e-29 | 0.023141 | 0 | 0.0081775 | 0 | 0.022498 | 2.1073e-28 | 0.0068659 | 0 | 0.019665 | 0 | 9.0236e-07 | 0.00017508 | 3.1491e-06 | 0.00055445 | 3.2303e-06 | 0.0003763 | 0.040532 | 0.025774 | 0.01506 | 0.0014492 | 5.895e-33 | 0.0012403 | 0 | 0.0013975 | 5.2682e-29 | 8.6654e-06 | 0.00045596 | 4.3228e-06 | 0.0013686 | 5.1982e-05 | 0.00052015 | 0.067812 | 0.0089772 | 0.08514 | 1.3483e-08 | 1.3887e-06 | 1.2276e-08 | 7.8252e-06 | 1.6166e-40 | 6.6235e-06 | 4.9149e-06 | 5.3972e-06 | 8.1275e-06 | 4.7148e-05 | 3.6343e-05 | 3.1418e-05 | 0.026744 | 0.020348 | 0.017483 | 7.7471e-06 | 4.2104e-07 | 3.2456e-05 | 1.9063e-07 | 4.0896e-06 | 3.1937e-06 | 0.00027526 | 0.001395 | 0.0027144
2 | 2.2 | 2.2.3 | Variance | 0.2284 | 0.11901 | 0.010201 | 0.026131 | 0.10955 | 0.19936 | 0.014678 | 1.4817e-29 | 0.049831 | 0 | 0.02049 | 3.5121e-29 | 0.068917 | 1.0536e-28 | 0.020544 | 0 | 0.048389 | 0 | 1.9267e-06 | 0.00073902 | 3.6673e-06 | 0.0010484 | 1.179e-06 | 0.00088274 | 0.074546 | 0.054437 | 0.015102 | 0.0035283 | 5.0912e-33 | 0.0030403 | 0 | 0.0050694 | 1.4049e-28 | 3.8026e-05 | 0.00017415 | 2.8932e-06 | 0.00061025 | 2.1528e-05 | 0.00062763 | 0.22381 | 0.0073877 | 0.017701 | 8.8288e-09 | 1.3321e-08 | 1.0794e-08 | 5.1239e-06 | 1.5508e-42 | 5.8238e-06 | 2.8911e-06 | 3.4296e-06 | 7.0971e-06 | 9.7148e-06 | 9.5847e-06 | 7.881e-06 | 0.0053863 | 0.0052439 | 0.0042004 | 2.1111e-06 | 1.2471e-06 | 1.7694e-07 | 9.5072e-07 | 4.2506e-05 | 1.2997e-06 | 0.00051612 | 0.013082 | 0.00037937
2 | 2.3 | 2.3.1 | Variance | 0.33291 | 0.23973 | 0.19918 | 0.018753 | 0.4294 | 0.4486 | 0.0087449 | 1.4817e-29 | 0.032033 | 0 | 0.010474 | 0 | 0.024564 | 2.1073e-28 | 0.0059822 | 0 | 0.01902 | 0 | 2.9737e-06 | 0.00038792 | 9.2164e-07 | 0.00028303 | 9.7585e-07 | 0.00076281 | 0.07682 | 0.01584 | 0.080423 | 0.0020885 | 2.6796e-34 | 0.0012565 | 0 | 0.0019168 | 2.1073e-28 | 1.5991e-06 | 0.0026364 | 6.1865e-05 | 0.0003465 | 1.4426e-05 | 0.00019399 | 0.048483 | 0.2914 | 0.02702 | 2.789e-08 | 7.8569e-06 | 4.801e-07 | 2.5702e-06 | 0.0022543 | 0.00025905 | 2.8063e-06 | 2.8183e-06 | 4.3098e-06 | 2.7432e-05 | 3.4126e-05 | 2.8165e-05 | 0.015545 | 0.01926 | 0.015806 | 8.868e-07 | 3.2285e-06 | 1.1531e-05 | 4.0236e-07 | 3.1864e-05 | 6.0549e-07 | 0.00018319 | 0.0099037 | 0.00069877
2 | 2.3 | 2.3.2 | Variance | 0.51725 | 0.39972 | 0.098396 | 0.029543 | 0.23087 | 0.2557 | 0.012713 | 1.7561e-29 | 0.033888 | 0 | 0.01401 | 0 | 0.048505 | 2.1073e-28 | 0.017428 | 0 | 0.050053 | 0 | 5.4464e-06 | 0.0012348 | 3.0294e-06 | 0.0021166 | 1.2657e-06 | 0.002861 | 0.13552 | 0.019401 | 0.14397 | 0.0022214 | 2.2776e-33 | 0.0037169 | 0 | 0.0034279 | 6.1463e-29 | 3.8558e-06 | 0.0036406 | 0.00010273 | 0.00055579 | 5.2374e-05 | 0.00097639 | 0.08503 | 0.66973 | 0.066948 | 2.1142e-08 | 1.5878e-06 | 2.7436e-07 | 1.9483e-06 | 0.00045567 | 0.00014806 | 2.4161e-06 | 2.9375e-06 | 4.2019e-06 | 2.1411e-05 | 1.9449e-05 | 1.8494e-05 | 0.012105 | 0.010862 | 0.010288 | 5.2411e-06 | 7.0004e-07 | 3.0583e-06 | 3.1665e-07 | 3.8409e-06 | 3.0093e-06 | 0.00019455 | 0.0010792 | 0.001379
2 | 2.3 | 2.3.3 | Variance | 0.67651 | 0.73675 | 0.065706 | 0.0090386 | 0.52929 | 0.48174 | 0.0072986 | 1.6463e-29 | 0.024614 | 0 | 0.0084633 | 0 | 0.025464 | 7.0243e-29 | 0.0084878 | 0 | 0.022686 | 0 | 5.3721e-06 | 0.00091132 | 1.933e-06 | 0.00062582 | 3.0218e-06 | 0.001062 | 0.35948 | 0.057374 | 0.07001 | 0.0015861 | 2.4116e-33 | 0.0013942 | 0 | 0.0015172 | 2.1073e-28 | 1.8927e-05 | 0.003691 | 5.4744e-05 | 0.00020143 | 3.5961e-05 | 0.00025503 | 0.40593 | 0.40325 | 0.066969 | 1.4016e-08 | 5.2312e-07 | 2.668e-07 | 1.2917e-06 | 0.00015014 | 0.00014399 | 2.2019e-06 | 2.6898e-06 | 3.8749e-06 | 2.4944e-05 | 1.8094e-05 | 1.7579e-05 | 0.014149 | 0.010105 | 0.0097755 | 4.2338e-06 | 3.7386e-07 | 1.5446e-05 | 2.0464e-07 | 4.7995e-06 | 7.7195e-06 | 0.00023648 | 0.0014656 | 0.0040954
2 | 2.4 | 2.4.1 | Variance | 0.67236 | 0.60495 | 0.23972 | 0.0054855 | 1.1681 | 1.199 | 0.011958 | 1.3171e-29 | 0.036114 | 0 | 0.011041 | 0 | 0.029088 | 1.4049e-28 | 0.0093738 | 0 | 0.031919 | 0 | 3.7479e-06 | 0.00081958 | 5.5738e-07 | 0.00071113 | 3.972e-06 | 0.00093145 | 0.24238 | 0.0041711 | 0.10839 | 0.0024411 | 6.9668e-33 | 0.0020744 | 0 | 0.0018631 | 2.1073e-28 | 1.1239e-05 | 0.00024258 | 7.062e-05 | 0.00024552 | 1.6714e-06 | 0.00027716 | 0.082186 | 0.4783 | 0.0092451 | 2.0354e-08 | 2.5421e-06 | 9.7188e-08 | 1.1813e-05 | 0.0007297 | 1.115e-41 | 3.0468e-06 | 3.169e-06 | 2.9328e-06 | 6.3097e-05 | 3.8149e-05 | 3.3914e-05 | 0.036099 | 0.021528 | 0.019191 | 2.804e-07 | 1.3236e-06 | 8.8108e-06 | 4.5101e-07 | 3.6084e-05 | 1.352e-06 | 0.00018118 | 0.011262 | 0.0010305
2 | 2.4 | 2.4.2 | Variance | 0.48766 | 0.41969 | 0.03451 | 0.0052625 | 0.47827 | 0.53459 | 0.012992 | 1.7561e-29 | 0.028398 | 0 | 0.0072229 | 0 | 0.02429 | 1.4049e-28 | 0.012213 | 0 | 0.044581 | 0 | 3.7742e-06 | 0.0012121 | 6.1866e-07 | 0.001071 | 4.6896e-06 | 0.0041943 | 0.10765 | 0.0041011 | 0.14945 | 0.0020281 | 8.0387e-33 | 0.0032247 | 0 | 0.0015333 | 2.1073e-28 | 5.9473e-06 | 0.00038367 | 7.6154e-05 | 0.0014472 | 8.3817e-07 | 0.00097823 | 0.034073 | 0.46437 | 0.00046913 | 9.5881e-08 | 2.1678e-07 | 1.1272e-08 | 5.5652e-05 | 6.2231e-05 | 1.293e-42 | 2.5558e-06 | 2.8899e-06 | 3.2174e-06 | 2.9549e-05 | 2.5718e-05 | 1.9738e-05 | 0.016769 | 0.014442 | 0.011047 | 4.3952e-06 | 1.0427e-06 | 2.7627e-05 | 2.2199e-06 | 9.4036e-06 | 1.0959e-05 | 0.0012221 | 0.0034596 | 0.0065004
2 | 2.4 | 2.4.3 | Variance | 0.41222 | 0.34053 | 0.019758 | 0.007324 | 0.38179 | 0.43971 | 0.016508 | 1.3171e-29 | 0.038199 | 0 | 0.0086162 | 0 | 0.023349 | 3.5121e-29 | 0.011645 | 0 | 0.048769 | 0 | 4.1861e-06 | 0.00039205 | 3.364e-07 | 0.00039856 | 3.0454e-06 | 0.00068671 | 0.10351 | 0.0041508 | 0.10624 | 0.0028422 | 9.6464e-33 | 0.0035473 | 0 | 0.0014818 | 2.1073e-28 | 6.9374e-06 | 0.00035024 | 5.1743e-05 | 0.00012888 | 9.886e-07 | 0.00044935 | 0.025237 | 0.24926 | 0.00058897 | 6.5351e-08 | 5.8187e-07 | 5.2695e-08 | 3.7931e-05 | 0.00016704 | 6.0448e-42 | 2.025e-06 | 2.4173e-06 | 3.1667e-06 | 1.4069e-05 | 1.7135e-05 | 1.6215e-05 | 0.0079189 | 0.0095735 | 0.0090368 | 1.305e-06 | 4.9006e-07 | 4.1151e-05 | 4.8958e-07 | 1.3485e-05 | 1.8907e-05 | 0.00025407 | 0.0043303 | 0.010724
1 | 1.1 | All | Variance | 0.011676 | 0.0055269 | 0.00011803 | 0.0023806 | 0.0072418 | 0.014072 | 0.038705 | 0 | 0.048236 | 0 | 0.0037223 | 0 | 0.01165 | 0.0014113 | 0.014302 | 0 | 0.11034 | 6.5356e-05 | 9.1344e-09 | 0.00048509 | 2.2e-08 | 0.0014314 | 1.6675e-09 | 0.0014606 | 0.0013714 | 0.0006678 | 0.0021423 | 0.003062 | 6.97e-08 | 0.0069865 | 6.6119e-05 | 0.00074832 | 0.0015119 | 5.1324e-09 | 0.00091925 | 1.252e-08 | 0.0056355 | 8.2011e-08 | 0.0045573 | 0.00068252 | 0.00048441 | 0.00078854 | 3.5255e-08 | 5.2803e-06 | 1.2881e-06 | 4.0435e-42 | 6.1479e-40 | 1.4775e-40 | 1.9162e-05 | 2.3992e-05 | 4.7629e-05 | 1.8219e-08 | 2.6494e-08 | 9.4685e-10 | 1.1819e-05 | 1.6314e-05 | 9.4588e-07 | 5.9333e-06 | 3.0771e-06 | 1.2504e-07 | 3.1474e-08 | 3.4761e-09 | 1.8424e-08 | 1.1362e-05 | 1.191e-06 | 6.462e-06
1 | 1.2 | All | Variance | 0.74701 | 0.73937 | 0.9631 | 0.00077423 | 0.016342 | 0.013817 | 0.0079909 | 0 | 0.024453 | 0 | 0.0093075 | 0 | 0.030768 | 0.00017076 | 0.009992 | 0 | 0.026658 | 0.00032606 | 2.7519e-06 | 0.013287 | 3.0014e-07 | 0.014723 | 1.8753e-07 | 0.013695 | 0.21675 | 0.026972 | 0.071407 | 0.0014448 | 6.2524e-06 | 0.0015893 | 0.00035079 | 0.0020077 | 0.00011709 | 8.7876e-06 | 0.0037498 | 1.2561e-05 | 0.0066619 | 8.3263e-06 | 0.00065428 | 0.13747 | 0.24412 | 0.020459 | 6.635e-07 | 8.9577e-05 | 4.9698e-07 | 7.6102e-41 | 1.0436e-38 | 5.7013e-41 | 6.2062e-05 | 7.6602e-05 | 0.00010992 | 0.00040702 | 0.00036104 | 0.00027786 | 0.22865 | 0.19986 | 0.15218 | 4.6397e-05 | 3.4539e-06 | 1.5442e-06 | 9.6323e-06 | 9.2955e-06 | 0.00032161 | 0.0070078 | 0.0023434 | 0.10554
1 | 1.3 | All | Variance | 1.5815 | 0.91136 | 0.23559 | 0.12384 | 1.9383 | 2.9492 | 0.01218 | 0 | 0.064963 | 0 | 0.02873 | 0 | 0.067339 | 5.4673e-07 | 0.011737 | 0 | 0.025665 | 0.0007312 | 7.5442e-05 | 0.096869 | 5.2618e-05 | 0.11941 | 0.00014772 | 0.080568 | 0.74664 | 0.042728 | 0.368 | 0.0046636 | 1.1072e-05 | 0.0017298 | 0.00089785 | 0.0046998 | 1.3455e-06 | 1.8659e-05 | 0.010655 | 0.0012795 | 0.10613 | 0.00090789 | 0.11162 | 0.37589 | 0.26598 | 0.021407 | 2.8335e-08 | 1.9619e-06 | 3.7712e-07 | 2.6112e-06 | 0.00017856 | 3.6427e-05 | 8.9256e-07 | 6.7245e-06 | 1.2091e-06 | 2.0675e-06 | 2.8695e-06 | 9.8982e-06 | 0.0011459 | 0.0014243 | 0.0055631 | 7.7741e-07 | 9.622e-07 | 0.00019899 | 1.5773e-07 | 0.00024018 | 8.369e-06 | 3.3671e-05 | 0.079238 | 0.011585
1 | 1.4 | All | Variance | 1.061 | 0.34956 | 0.050907 | 0.29089 | 0.23101 | 0.69919 | 0.007975 | 0 | 0.031175 | 0 | 0.006886 | 0 | 0.0063461 | 0.00070436 | 0.0017953 | 0 | 0.012414 | 0.000984 | 5.9209e-06 | 0.00026884 | 6.0058e-07 | 0.00068914 | 8.2977e-07 | 0.0020821 | 0.25485 | 0.14849 | 0.04013 | 0.0024944 | 2.2572e-06 | 0.0013644 | 0.0010658 | 0.0037215 | 0.00075764 | 7.1302e-05 | 0.0028537 | 1.7896e-05 | 0.00079415 | 6.1389e-05 | 0.0006933 | 0.32902 | 0.034628 | 0.25877 | 4.9738e-07 | 3.5985e-08 | 1.1647e-06 | 0.00014522 | 1.0327e-05 | 0.00034514 | 3.1369e-06 | 5.1543e-06 | 8.2245e-06 | 1.0019e-05 | 1.8497e-05 | 1.4813e-06 | 0.0055373 | 0.010183 | 0.00072022 | 4.5335e-06 | 4.4351e-06 | 4.7832e-06 | 6.7021e-07 | 1.1869e-05 | 1.3661e-07 | 0.00035876 | 0.0042573 | 2.4911e-05
2 | 2.1 | All | Variance | 0.010516 | 0.00013444 | 1.6398e-05 | 0.012995 | 0.00024238 | 0.0097033 | 0.046135 | 0 | 0.16253 | 0 | 0.073808 | 0 | 0.25779 | 0.0002284 | 0.077274 | 0 | 0.17134 | 0.00027235 | 1.3834e-07 | 0.00014599 | 2.9737e-07 | 0.0012713 | 1.3141e-07 | 0.00041057 | 0.0032496 | 0.0011939 | 0.00017692 | 0.01033 | 2.5007e-07 | 0.010891 | 0.00021473 | 0.016364 | 0.00013873 | 4.6731e-08 | 0.0040001 | 1.9152e-06 | 0.064375 | 1.1024e-06 | 0.011908 | 1.1461e-05 | 7.7359e-05 | 3.9886e-05 | 1.0839e-08 | 9.3395e-08 | 6.6889e-07 | 1.2431e-42 | 1.0872e-41 | 7.6714e-41 | 5.3648e-06 | 9.0853e-06 | 2.7315e-05 | 3.093e-08 | 2.9061e-08 | 3.1583e-09 | 1.7606e-05 | 1.6766e-05 | 2.1519e-06 | 3.5764e-06 | 1.4166e-06 | 1.5452e-07 | 1.0829e-10 | 4.2464e-09 | 1.3297e-10 | 3.8795e-08 | 1.4672e-06 | 4.5775e-08
2 | 2.2 | All | Variance | 0.5431 | 2.3724 | 4.0813 | 1.2348 | 12.6724 | 6.9046 | 0.0050679 | 0 | 0.0087347 | 0 | 0.0090228 | 0 | 0.06362 | 0.0011335 | 0.025081 | 0 | 0.045231 | 0.00029325 | 5.292e-06 | 0.049777 | 4.4993e-05 | 0.046116 | 8.1276e-05 | 0.022203 | 0.18993 | 0.19933 | 0.1808 | 0.00019546 | 1.5732e-05 | 0.002712 | 0.00029401 | 0.00085863 | 0.00086658 | 3.5231e-05 | 0.027887 | 2.005e-05 | 0.001621 | 0.0012018 | 0.058534 | 1.5484 | 0.22438 | 0.60937 | 2.5471e-07 | 9.3176e-07 | 1.3406e-07 | 0.00014782 | 1.0847e-40 | 7.2333e-05 | 0.0001522 | 0.00017542 | 0.00030496 | 0.00075147 | 0.00070501 | 0.00095027 | 0.42112 | 0.39014 | 0.5263 | 3.1329e-05 | 1.1668e-05 | 4.0384e-05 | 6.8783e-07 | 2.9958e-07 | 1.6869e-07 | 0.0012452 | 0.00026083 | 0.00073351
2 | 2.3 | All | Variance | 0.94478 | 0.21143 | 0.22022 | 0.26319 | 0.017688 | 0.27948 | 0.0071454 | 0 | 0.0033564 | 0 | 0.00018264 | 0 | 0.0021545 | 7.1671e-05 | 0.0033174 | 0 | 0.026419 | 0.00026358 | 3.8132e-06 | 0.0010812 | 2.8974e-06 | 0.0013311 | 1.6462e-06 | 0.0061081 | 0.10381 | 0.0014572 | 0.37868 | 0.00028027 | 1.6049e-07 | 0.0028307 | 0.00026521 | 0.00045564 | 8.1856e-05 | 4.2128e-06 | 0.00024757 | 7.0176e-05 | 0.0016268 | 6.1527e-05 | 0.0012636 | 0.032229 | 0.44727 | 0.057425 | 5.8698e-08 | 1.043e-05 | 6.8995e-06 | 5.4093e-06 | 0.0029929 | 0.0037233 | 1.3209e-05 | 1.6747e-05 | 4.1949e-05 | 4.6203e-05 | 3.531e-05 | 4.3523e-05 | 0.025623 | 0.019137 | 0.023087 | 4.3619e-07 | 1.8028e-05 | 3.4903e-06 | 4.6941e-08 | 2.5982e-05 | 3.2562e-06 | 1.6719e-05 | 0.0066298 | 0.0015162
2 | 2.4 | All | Variance | 0.41204 | 0.58272 | 0.33678 | 0.034225 | 1.7427 | 1.3726 | 0.0003178 | 0 | 0.00021052 | 0 | 0.00021651 | 0 | 0.0014939 | 0.00030027 | 0.0012443 | 0 | 0.0036338 | 0.00030032 | 3.5182e-06 | 0.0033924 | 3.5707e-06 | 0.0008713 | 4.004e-06 | 0.0035056 | 0.21371 | 0.23806 | 0.18536 | 7.6624e-05 | 3.5071e-07 | 0.00023145 | 0.00030846 | 0.00011456 | 0.00027087 | 4.992e-05 | 0.0061473 | 5.4422e-05 | 0.0021136 | 1.5473e-06 | 0.0022813 | 1.3682 | 0.22466 | 0.0022594 | 2.6433e-07 | 1.1707e-06 | 1.34e-06 | 0.00015342 | 0.00033606 | 1.5372e-40 | 1.945e-05 | 2.056e-05 | 2.6468e-05 | 0.0001543 | 0.00013532 | 3.6823e-05 | 0.087085 | 0.075615 | 0.019781 | 2.9238e-06 | 4.2911e-06 | 3.8979e-06 | 9.7623e-07 | 3.91e-05 | 9.9901e-06 | 0.00056696 | 0.011392 | 0.0040785
1 | 1.1 | 1.1.1 | Standard Deviation | 0.056611 | 0.056698 | 0.010138 | 0.045475 | 0.062894 | 0.063329 | 0.17545 | 3.6291e-15 | 0.23871 | 0 | 0.10062 | 0 | 0.16575 | 1.4516e-14 | 0.11104 | 0 | 0.2744 | 0 | 0.00043326 | 0.017487 | 0.00033262 | 0.052831 | 0.00024874 | 0.025433 | 0.036331 | 0.039724 | 0.020567 | 0.060232 | 3.5023e-19 | 0.069139 | 0 | 0.041907 | 5.1324e-15 | 8.5121e-05 | 0.042018 | 0.00048519 | 0.066272 | 0.00058949 | 0.030286 | 0.012035 | 0.02236 | 0.02563 | 0.00018199 | 0.00036849 | 0.00023358 | 1.949e-21 | 3.9763e-21 | 2.5016e-21 | 0.00050907 | 0.00047986 | 0.00060747 | 0.00023811 | 0.00022859 | 0.00012266 | 0.0057852 | 0.0055289 | 0.0029651 | 0.000275 | 0.0003151 | 8.9268e-05 | 7.5252e-05 | 8.267e-05 | 0.00015016 | 0.001427 | 0.0015384 | 0.0028081
1 | 1.1 | 1.1.2 | Standard Deviation | 0.052519 | 0.025401 | 0.0092841 | 0.042945 | 0.025826 | 0.049512 | 0.11064 | 4.0575e-15 | 0.19315 | 0 | 0.10657 | 0 | 0.18209 | 1.3252e-14 | 0.10622 | 0 | 0.18489 | 0 | 0.00026534 | 0.011274 | 0.00029659 | 0.02366 | 0.00022609 | 0.019043 | 0.03043 | 0.021536 | 0.012753 | 0.048858 | 2.022e-19 | 0.04664 | 0 | 0.045994 | 8.3811e-15 | 0.00010059 | 0.022826 | 0.00060238 | 0.095197 | 0.00065573 | 0.048434 | 0.0072172 | 0.010502 | 0.012207 | 0.000248 | 0.00032332 | 0.00017634 | 2.6559e-21 | 3.4887e-21 | 1.8886e-21 | 0.00064381 | 0.00076242 | 0.0010949 | 0.00016007 | 0.00015789 | 0.00017185 | 0.0038853 | 0.0038214 | 0.0041592 | 0.00036347 | 0.00023608 | 0.0001011 | 5.2797e-05 | 0.00010806 | 0.00016957 | 0.0010018 | 0.0020107 | 0.003172
1 | 1.1 | 1.1.3 | Standard Deviation | 0.048365 | 0.019075 | 0.0074346 | 0.043533 | 0.020201 | 0.049776 | 0.1062 | 4.0575e-15 | 0.17931 | 0 | 0.11585 | 0 | 0.19132 | 8.3811e-15 | 0.095854 | 0 | 0.18151 | 0 | 0.00030808 | 0.01209 | 0.00040833 | 0.027952 | 0.00026685 | 0.033131 | 0.031384 | 0.037219 | 0.022172 | 0.045078 | 1.4996e-19 | 0.045652 | 0 | 0.048156 | 7.2582e-15 | 9.0995e-05 | 0.019355 | 0.00057323 | 0.079051 | 0.00051998 | 0.031113 | 0.0063331 | 0.0095018 | 0.010761 | 7.9638e-05 | 0.00018095 | 0.00018214 | 8.5287e-22 | 1.9525e-21 | 1.9506e-21 | 0.00061849 | 0.00072059 | 0.00099945 | 0.00016806 | 0.00026323 | 0.00013341 | 0.0040712 | 0.0063803 | 0.0032184 | 0.00033755 | 0.00022196 | 4.6502e-05 | 9.8934e-05 | 5.8651e-05 | 0.00014245 | 0.001877 | 0.0010912 | 0.0026643
1 | 1.2 | 1.2.1 | Standard Deviation | 0.40624 | 0.39104 | 0.41824 | 0.057749 | 0.070614 | 0.084213 | 0.12161 | 3.8493e-15 | 0.2021 | 0 | 0.11636 | 0 | 0.20716 | 1.3252e-14 | 0.12515 | 0 | 0.21963 | 0 | 0.0013229 | 0.14152 | 0.0014866 | 0.15945 | 0.001596 | 0.1167 | 0.19433 | 0.092852 | 0.16666 | 0.050564 | 1.9195e-17 | 0.054895 | 0 | 0.05187 | 1.4516e-14 | 0.0010962 | 0.029028 | 0.0021314 | 0.042991 | 0.0033749 | 0.074387 | 0.11504 | 0.21437 | 0.065808 | 0.00027674 | 0.0025723 | 0.00034101 | 2.9639e-21 | 2.777e-20 | 3.6525e-21 | 0.0014408 | 0.0016276 | 0.0014722 | 0.0057001 | 0.0055539 | 0.0053083 | 0.13607 | 0.13183 | 0.12631 | 0.001616 | 0.0017161 | 0.0024548 | 0.00096983 | 0.0053935 | 0.0016667 | 0.023747 | 0.091856 | 0.039257
1 | 1.2 | 1.2.2 | Standard Deviation | 0.1566 | 0.13838 | 0.1436 | 0.046391 | 0.04363 | 0.050392 | 0.11184 | 3.6291e-15 | 0.19305 | 0 | 0.12021 | 0 | 0.21994 | 1.0265e-14 | 0.12286 | 0 | 0.20131 | 0 | 0.00080844 | 0.092041 | 0.00082194 | 0.10529 | 0.001007 | 0.08902 | 0.073784 | 0.074779 | 0.050972 | 0.048958 | 1.4176e-17 | 0.050918 | 0 | 0.055703 | 1.4516e-14 | 0.0014042 | 0.025227 | 0.0014792 | 0.030308 | 0.0016299 | 0.048174 | 0.048935 | 0.063251 | 0.062653 | 0.00017661 | 0.0011792 | 0.00033158 | 1.8914e-21 | 1.2727e-20 | 3.5514e-21 | 0.0011489 | 0.0012686 | 0.0015519 | 0.0027158 | 0.002877 | 0.0021393 | 0.064262 | 0.067756 | 0.049783 | 0.0025759 | 9.0747e-05 | 0.00044919 | 0.00076373 | 0.00031229 | 0.0027558 | 0.023465 | 0.0057808 | 0.048801
1 | 1.2 | 1.2.3 | Standard Deviation | 0.1106 | 0.10946 | 0.11185 | 0.036688 | 0.029352 | 0.052447 | 0.059876 | 4.0575e-15 | 0.10159 | 0 | 0.076921 | 0 | 0.20518 | 8.3811e-15 | 0.11974 | 0 | 0.13814 | 0 | 0.00066627 | 0.044866 | 0.00047848 | 0.037993 | 0.00056751 | 0.028298 | 0.072289 | 0.047758 | 0.061097 | 0.025675 | 2.2415e-17 | 0.034968 | 0 | 0.051906 | 1.4516e-14 | 0.002173 | 0.043177 | 0.0018308 | 0.033626 | 0.0024981 | 0.030917 | 0.024293 | 0.031028 | 0.076556 | 0.00011611 | 0.00067614 | 0.00014672 | 1.2435e-21 | 7.2966e-21 | 1.5715e-21 | 0.00096245 | 0.0010651 | 0.0016147 | 0.0018027 | 0.0014796 | 0.00092336 | 0.042405 | 0.03439 | 0.020607 | 0.00090502 | 0.00021438 | 0.00065342 | 0.00049935 | 0.00044524 | 0.0036904 | 0.011902 | 0.0079312 | 0.064937
1 | 1.3 | 1.3.1 | Standard Deviation | 0.22843 | 0.26089 | 0.32724 | 0.057547 | 0.089137 | 0.12982 | 0.083496 | 3.6291e-15 | 0.13954 | 0 | 0.077404 | 0 | 0.13206 | 7.8398e-15 | 0.078803 | 0 | 0.14356 | 0 | 0.00063644 | 0.024935 | 0.00067026 | 0.018057 | 0.00064143 | 0.020417 | 0.12091 | 0.075446 | 0.08056 | 0.035343 | 4.3309e-17 | 0.036708 | 0 | 0.03511 | 1.4516e-14 | 0.0017069 | 0.022664 | 0.002011 | 0.020553 | 0.0031473 | 0.017447 | 0.093383 | 0.14294 | 0.1463 | 0.0002027 | 0.00033064 | 0.00055197 | 0.0019459 | 0.0031544 | 0.0054249 | 0.0013515 | 0.0014929 | 0.001392 | 0.0054342 | 0.005016 | 0.004317 | 0.12973 | 0.11904 | 0.10248 | 0.00098084 | 0.0011246 | 0.0031694 | 0.0010444 | 0.0070546 | 0.0018187 | 0.022582 | 0.12509 | 0.044889
1 | 1.3 | 1.3.2 | Standard Deviation | 0.44566 | 0.3799 | 0.40149 | 0.11356 | 0.16371 | 0.22613 | 0.32143 | 3.8493e-15 | 0.5515 | 0 | 0.32395 | 0 | 0.57928 | 1.3252e-14 | 0.33941 | 0 | 0.57512 | 0 | 0.001089 | 0.069463 | 0.00086311 | 0.076154 | 0.0010136 | 0.070988 | 0.16685 | 0.17703 | 0.15965 | 0.13961 | 2.5882e-17 | 0.14587 | 0 | 0.14614 | 1.4516e-14 | 0.0028791 | 0.037308 | 0.0040353 | 0.02946 | 0.0034912 | 0.032004 | 0.13855 | 0.18223 | 0.1378 | 0.00012166 | 0.00041634 | 0.00026237 | 0.0011679 | 0.0039718 | 0.0025786 | 0.0014243 | 0.0015686 | 0.0014475 | 0.0047901 | 0.0051426 | 0.0045896 | 0.11408 | 0.122 | 0.109 | 0.00043218 | 0.0010778 | 0.0019078 | 0.00091107 | 0.0089309 | 0.0014289 | 0.017927 | 0.15879 | 0.032616
1 | 1.3 | 1.3.3 | Standard Deviation | 0.88712 | 0.79382 | 0.2587 | 0.09839 | 0.68483 | 0.77699 | 0.1031 | 3.8493e-15 | 0.14961 | 0 | 0.079375 | 0 | 0.15891 | 1.4516e-14 | 0.11113 | 0 | 0.20054 | 0 | 0.0018155 | 0.027209 | 0.00075405 | 0.03453 | 0.0013766 | 0.048127 | 0.39766 | 0.086133 | 0.46251 | 0.038224 | 2.5882e-17 | 0.049541 | 0 | 0.03857 | 1.4516e-14 | 0.001427 | 0.038575 | 0.007301 | 0.033179 | 0.0029029 | 0.03491 | 0.19854 | 0.65719 | 0.097363 | 9.5836e-05 | 0.00029787 | 0.00033729 | 0.00092 | 0.0028417 | 0.0033149 | 0.0013105 | 0.0014664 | 0.0015042 | 0.0034781 | 0.00445 | 0.0042431 | 0.082528 | 0.10541 | 0.10057 | 0.001248 | 0.00096527 | 0.0021161 | 0.0011217 | 0.0046886 | 0.0015002 | 0.025252 | 0.083574 | 0.033752
1 | 1.4 | 1.4.1 | Standard Deviation | 0.91946 | 0.71468 | 0.31612 | 0.23081 | 0.49937 | 0.6676 | 0.092467 | 4.0575e-15 | 0.15138 | 0 | 0.089809 | 0 | 0.16533 | 1.4516e-14 | 0.10336 | 0 | 0.17792 | 0 | 0.0015934 | 0.031602 | 0.001079 | 0.052553 | 0.0011239 | 0.061635 | 0.34281 | 0.25269 | 0.45525 | 0.038222 | 4.63e-17 | 0.045916 | 0 | 0.043192 | 1.4516e-14 | 0.0020326 | 0.020899 | 0.0070801 | 0.025517 | 0.0031834 | 0.041595 | 0.24949 | 0.61761 | 0.21799 | 0.00025582 | 0.00060633 | 0.0003193 | 0.0043713 | 0.010272 | 0.0054963 | 0.0014867 | 0.001606 | 0.0016295 | 0.0040722 | 0.0046444 | 0.0043006 | 0.096681 | 0.10997 | 0.10183 | 0.0010009 | 0.00098989 | 0.0013687 | 0.00065434 | 0.0043089 | 0.0017756 | 0.015465 | 0.075101 | 0.032811
1 | 1.4 | 1.4.2 | Standard Deviation | 1.6086 | 1.4818 | 0.30435 | 0.13884 | 1.2053 | 1.3315 | 0.11378 | 3.6291e-15 | 0.20732 | 0 | 0.11807 | 0 | 0.20673 | 5.9263e-15 | 0.11048 | 0 | 0.17763 | 0 | 0.0030625 | 0.02993 | 0.0011157 | 0.033582 | 0.0019705 | 0.047459 | 0.58952 | 0.34766 | 0.69729 | 0.053895 | 4.1734e-17 | 0.046171 | 0 | 0.0536 | 1.4516e-14 | 0.0052169 | 0.049489 | 0.01177 | 0.021552 | 0.0029105 | 0.02793 | 0.30998 | 0.97938 | 0.2259 | 0.00092862 | 0.001099 | 0.00024725 | 0.015868 | 0.018619 | 0.0042562 | 0.0014365 | 0.001582 | 0.0016819 | 0.0041448 | 0.0043711 | 0.00361 | 0.098522 | 0.10342 | 0.085114 | 0.0018187 | 0.0015293 | 0.0020706 | 0.00070819 | 0.0056982 | 0.0021813 | 0.019524 | 0.098439 | 0.047123
1 | 1.4 | 1.4.3 | Standard Deviation | 0.40315 | 0.41139 | 0.17696 | 0.10334 | 0.52204 | 0.48766 | 0.11103 | 4.6852e-15 | 0.2071 | 0 | 0.11762 | 0 | 0.19626 | 1.0265e-14 | 0.11832 | 0 | 0.19771 | 0 | 0.001633 | 0.047242 | 0.0013535 | 0.023874 | 0.0019258 | 0.021416 | 0.28103 | 0.21323 | 0.30335 | 0.053466 | 5.6705e-17 | 0.049738 | 0 | 0.048743 | 1.4516e-14 | 0.0045857 | 0.021302 | 0.0095185 | 0.012542 | 0.0040148 | 0.022477 | 0.301 | 0.7104 | 0.066785 | 9.0209e-05 | 0.00067151 | 0.00028666 | 0.0015415 | 0.011376 | 0.0049346 | 0.0014273 | 0.0015638 | 0.001679 | 0.0049299 | 0.0043675 | 0.0037331 | 0.11743 | 0.10332 | 0.088091 | 0.0018893 | 0.0003442 | 0.0014706 | 0.00065284 | 0.0063781 | 0.0017916 | 0.017887 | 0.11593 | 0.037631
2 | 2.1 | 2.1.1 | Standard Deviation | 0.057675 | 0.03721 | 0.008111 | 0.041713 | 0.040126 | 0.059192 | 0.13054 | 4.6852e-15 | 0.17995 | 0 | 0.098627 | 0 | 0.15964 | 1.4516e-14 | 0.094493 | 0 | 0.22193 | 0 | 0.000355 | 0.011981 | 0.00035935 | 0.034778 | 0.00025519 | 0.022059 | 0.035342 | 0.03022 | 0.016983 | 0.045352 | 2.1684e-19 | 0.055961 | 0 | 0.040007 | 1.4516e-14 | 7.0896e-05 | 0.020187 | 0.000638 | 0.070554 | 0.00067405 | 0.041548 | 0.0068024 | 0.015382 | 0.019093 | 9.4839e-05 | 0.00015789 | 0.00014981 | 1.0157e-21 | 1.7035e-21 | 1.6044e-21 | 0.00057847 | 0.00048886 | 0.00079213 | 0.0001886 | 0.00017993 | 0.00017167 | 0.0045728 | 0.0043542 | 0.0041675 | 0.00027926 | 0.00019867 | 4.8858e-05 | 8.2652e-05 | 7.6912e-05 | 0.00017529 | 0.0015678 | 0.0014311 | 0.0032783
2 | 2.1 | 2.1.2 | Standard Deviation | 0.042395 | 0.021025 | 0.01032 | 0.036144 | 0.023159 | 0.046014 | 0.1069 | 4.1906e-15 | 0.16292 | 0 | 0.095817 | 0 | 0.17753 | 8.8895e-15 | 0.099081 | 0 | 0.18226 | 0 | 0.00034028 | 0.018244 | 0.00035585 | 0.032424 | 0.00029888 | 0.021382 | 0.028374 | 0.027644 | 0.010989 | 0.040762 | 1.4996e-19 | 0.045722 | 5.9263e-15 | 0.044558 | 1.1853e-14 | 7.4091e-05 | 0.021884 | 0.00021837 | 0.031192 | 0.00027523 | 0.016644 | 0.010558 | 0.0072866 | 0.011234 | 7.1516e-05 | 0.00011324 | 0.0003409 | 7.659e-22 | 1.2218e-21 | 3.6508e-21 | 0.00049791 | 0.0004137 | 0.00068389 | 0.0002036 | 0.00022033 | 0.00015929 | 0.0049326 | 0.0053292 | 0.0038595 | 0.00024293 | 0.00016636 | 8.1684e-05 | 6.4936e-05 | 0.00010841 | 0.00011373 | 0.0012319 | 0.0020166 | 0.0021271
2 | 2.1 | 2.1.3 | Standard Deviation | 0.044339 | 0.022243 | 0.007269 | 0.033724 | 0.023545 | 0.04398 | 0.086262 | 3.6291e-15 | 0.15492 | 0 | 0.090458 | 5.9263e-15 | 0.15228 | 1.4516e-14 | 0.079977 | 0 | 0.13738 | 0 | 0.00037125 | 0.012358 | 0.00037136 | 0.032533 | 0.00028782 | 0.019079 | 0.032114 | 0.020726 | 0.010731 | 0.038879 | 9.0429e-20 | 0.034501 | 0 | 0.038241 | 4.1906e-15 | 8.4029e-05 | 0.018432 | 0.00054331 | 0.076154 | 0.00052259 | 0.032532 | 0.0057958 | 0.009241 | 0.012853 | 7.4112e-05 | 0.00080315 | 0.00012047 | 7.937e-22 | 8.6657e-21 | 1.2901e-21 | 0.00020317 | 0.00036518 | 0.000515 | 0.0001347 | 0.00017943 | 0.00013696 | 0.0032669 | 0.004344 | 0.0033084 | 0.00019946 | 0.00015279 | 9.7271e-05 | 9.7066e-05 | 7.3283e-05 | 0.00010349 | 0.0018418 | 0.0013634 | 0.0019355
2 | 2.2 | 2.2.1 | Standard Deviation | 0.56059 | 0.34962 | 0.68475 | 0.23981 | 1.0226 | 1.2251 | 0.15448 | 3.6291e-15 | 0.26342 | 0 | 0.16357 | 0 | 0.30854 | 1.4516e-14 | 0.17991 | 0 | 0.29052 | 0 | 0.0012866 | 0.012808 | 0.002694 | 0.01874 | 0.0028321 | 0.024795 | 0.15057 | 0.19775 | 0.31921 | 0.065431 | 6.6493e-17 | 0.072295 | 0 | 0.088771 | 1.3252e-14 | 0.0037157 | 0.057251 | 0.0027221 | 0.062479 | 0.011696 | 0.025471 | 0.25536 | 0.14526 | 0.2558 | 7.6242e-05 | 0.00051706 | 0.00027991 | 0.0018367 | 5.5788e-21 | 0.0065018 | 0.0024703 | 0.002575 | 0.0028929 | 0.0096463 | 0.009029 | 0.010922 | 0.23063 | 0.21484 | 0.26084 | 0.0010835 | 0.00076649 | 0.0028381 | 0.00069417 | 0.0014819 | 0.0013706 | 0.013872 | 0.026741 | 0.029235
2 | 2.2 | 2.2.2 | Standard Deviation | 0.32949 | 0.42454 | 0.35501 | 0.2236 | 0.71263 | 0.54905 | 0.08198 | 3.6291e-15 | 0.15212 | 0 | 0.090429 | 0 | 0.14999 | 1.4516e-14 | 0.082861 | 0 | 0.14023 | 0 | 0.00094993 | 0.013232 | 0.0017746 | 0.023547 | 0.0017973 | 0.019399 | 0.20133 | 0.16054 | 0.12272 | 0.038068 | 7.6779e-17 | 0.035218 | 0 | 0.037383 | 7.2582e-15 | 0.0029437 | 0.021353 | 0.0020791 | 0.036994 | 0.0072099 | 0.022807 | 0.26041 | 0.094748 | 0.29179 | 0.00011612 | 0.0011784 | 0.0001108 | 0.0027974 | 1.2715e-20 | 0.0025736 | 0.002217 | 0.0023232 | 0.0028509 | 0.0068664 | 0.0060286 | 0.0056052 | 0.16354 | 0.14265 | 0.13222 | 0.0027834 | 0.00064888 | 0.005697 | 0.00043661 | 0.0020223 | 0.0017871 | 0.016591 | 0.03735 | 0.0521
2 | 2.2 | 2.2.3 | Standard Deviation | 0.47791 | 0.34497 | 0.101 | 0.16165 | 0.33099 | 0.4465 | 0.12115 | 3.8493e-15 | 0.22323 | 0 | 0.14314 | 5.9263e-15 | 0.26252 | 1.0265e-14 | 0.14333 | 0 | 0.21997 | 0 | 0.0013881 | 0.027185 | 0.001915 | 0.032379 | 0.0010858 | 0.029711 | 0.27303 | 0.23332 | 0.12289 | 0.0594 | 7.1352e-17 | 0.055139 | 0 | 0.0712 | 1.1853e-14 | 0.0061665 | 0.013196 | 0.0017009 | 0.024703 | 0.0046398 | 0.025053 | 0.47308 | 0.085952 | 0.13305 | 9.3962e-05 | 0.00011542 | 0.00010389 | 0.0022636 | 1.2453e-21 | 0.0024133 | 0.0017003 | 0.0018519 | 0.002664 | 0.0031169 | 0.0030959 | 0.0028073 | 0.073391 | 0.072415 | 0.064811 | 0.0014529 | 0.0011168 | 0.00042064 | 0.00097505 | 0.0065197 | 0.00114 | 0.022718 | 0.11438 | 0.019477
2 | 2.3 | 2.3.1 | Standard Deviation | 0.57699 | 0.48962 | 0.4463 | 0.13694 | 0.65529 | 0.66978 | 0.093514 | 3.8493e-15 | 0.17898 | 0 | 0.10234 | 0 | 0.15673 | 1.4516e-14 | 0.077344 | 0 | 0.13791 | 0 | 0.0017244 | 0.019696 | 0.00096002 | 0.016823 | 0.00098785 | 0.027619 | 0.27716 | 0.12586 | 0.28359 | 0.0457 | 1.6369e-17 | 0.035447 | 0 | 0.043781 | 1.4516e-14 | 0.0012646 | 0.051346 | 0.0078654 | 0.018615 | 0.0037982 | 0.013928 | 0.22019 | 0.53982 | 0.16438 | 0.000167 | 0.002803 | 0.00069289 | 0.0016032 | 0.047479 | 0.016095 | 0.0016752 | 0.0016788 | 0.002076 | 0.0052376 | 0.0058417 | 0.005307 | 0.12468 | 0.13878 | 0.12572 | 0.0009417 | 0.0017968 | 0.0033957 | 0.00063432 | 0.0056448 | 0.00077813 | 0.013535 | 0.099517 | 0.026434
2 | 2.3 | 2.3.2 | Standard Deviation | 0.7192 | 0.63224 | 0.31368 | 0.17188 | 0.48049 | 0.50567 | 0.11275 | 4.1906e-15 | 0.18409 | 0 | 0.11836 | 0 | 0.22024 | 1.4516e-14 | 0.13202 | 0 | 0.22372 | 0 | 0.0023338 | 0.03514 | 0.0017405 | 0.046007 | 0.001125 | 0.053488 | 0.36813 | 0.13929 | 0.37943 | 0.047132 | 4.7724e-17 | 0.060967 | 0 | 0.058548 | 7.8398e-15 | 0.0019636 | 0.060337 | 0.010136 | 0.023575 | 0.007237 | 0.031247 | 0.2916 | 0.81837 | 0.25874 | 0.0001454 | 0.0012601 | 0.00052379 | 0.0013958 | 0.021346 | 0.012168 | 0.0015544 | 0.0017139 | 0.0020499 | 0.0046272 | 0.0044101 | 0.0043005 | 0.11002 | 0.10422 | 0.10143 | 0.0022894 | 0.00083668 | 0.0017488 | 0.00056272 | 0.0019598 | 0.0017347 | 0.013948 | 0.032851 | 0.037135
2 | 2.3 | 2.3.3 | Standard Deviation | 0.8225 | 0.85834 | 0.25633 | 0.095072 | 0.72753 | 0.69407 | 0.085432 | 4.0575e-15 | 0.15689 | 0 | 0.091996 | 0 | 0.15957 | 8.3811e-15 | 0.092129 | 0 | 0.15062 | 0 | 0.0023178 | 0.030188 | 0.0013903 | 0.025016 | 0.0017383 | 0.032589 | 0.59957 | 0.23953 | 0.26459 | 0.039826 | 4.9108e-17 | 0.037339 | 0 | 0.038952 | 1.4516e-14 | 0.0043505 | 0.060754 | 0.0073989 | 0.014192 | 0.0059967 | 0.01597 | 0.63712 | 0.63502 | 0.25878 | 0.00011839 | 0.00072327 | 0.00051653 | 0.0011365 | 0.012253 | 0.012 | 0.0014839 | 0.0016401 | 0.0019685 | 0.0049944 | 0.0042537 | 0.0041928 | 0.11895 | 0.10053 | 0.098871 | 0.0020576 | 0.00061144 | 0.0039301 | 0.00045237 | 0.0021908 | 0.0027784 | 0.015378 | 0.038283 | 0.063995
2 | 2.4 | 2.4.1 | Standard Deviation | 0.81997 | 0.77779 | 0.48962 | 0.074064 | 1.0808 | 1.095 | 0.10935 | 3.6291e-15 | 0.19004 | 0 | 0.10508 | 0 | 0.17055 | 1.1853e-14 | 0.096818 | 0 | 0.17866 | 0 | 0.0019359 | 0.028628 | 0.00074658 | 0.026667 | 0.001993 | 0.03052 | 0.49232 | 0.064584 | 0.32922 | 0.049407 | 8.3468e-17 | 0.045545 | 0 | 0.043164 | 1.4516e-14 | 0.0033525 | 0.015575 | 0.0084036 | 0.015669 | 0.0012928 | 0.016648 | 0.28668 | 0.69159 | 0.096151 | 0.00014267 | 0.0015944 | 0.00031175 | 0.0034371 | 0.027013 | 3.3391e-21 | 0.0017455 | 0.0017802 | 0.0017126 | 0.0079434 | 0.0061765 | 0.0058236 | 0.19 | 0.14672 | 0.13853 | 0.00052953 | 0.0011505 | 0.0029683 | 0.00067158 | 0.006007 | 0.0011628 | 0.01346 | 0.10612 | 0.032101
2 | 2.4 | 2.4.2 | Standard Deviation | 0.69833 | 0.64783 | 0.18577 | 0.072543 | 0.69157 | 0.73116 | 0.11398 | 4.1906e-15 | 0.16852 | 0 | 0.084987 | 0 | 0.15585 | 1.1853e-14 | 0.11051 | 0 | 0.21114 | 0 | 0.0019427 | 0.034815 | 0.00078655 | 0.032726 | 0.0021655 | 0.064763 | 0.32811 | 0.06404 | 0.38658 | 0.045035 | 8.9659e-17 | 0.056787 | 0 | 0.039158 | 1.4516e-14 | 0.0024387 | 0.019588 | 0.0087266 | 0.038043 | 0.00091551 | 0.031277 | 0.18459 | 0.68144 | 0.021659 | 0.00030965 | 0.0004656 | 0.00010617 | 0.00746 | 0.0078886 | 1.1371e-21 | 0.0015987 | 0.0017 | 0.0017937 | 0.0054359 | 0.0050713 | 0.0044427 | 0.12949 | 0.12018 | 0.1051 | 0.0020965 | 0.0010211 | 0.0052561 | 0.0014899 | 0.0030665 | 0.0033105 | 0.034959 | 0.058819 | 0.080625
2 | 2.4 | 2.4.3 | Standard Deviation | 0.64204 | 0.58355 | 0.14056 | 0.08558 | 0.61789 | 0.6631 | 0.12849 | 3.6291e-15 | 0.19545 | 0 | 0.092824 | 0 | 0.15281 | 5.9263e-15 | 0.10791 | 0 | 0.22084 | 0 | 0.002046 | 0.0198 | 0.00058 | 0.019964 | 0.0017451 | 0.026205 | 0.32174 | 0.064427 | 0.32594 | 0.053312 | 9.8216e-17 | 0.059559 | 0 | 0.038494 | 1.4516e-14 | 0.0026339 | 0.018715 | 0.0071933 | 0.011352 | 0.00099428 | 0.021198 | 0.15886 | 0.49926 | 0.024269 | 0.00025564 | 0.00076281 | 0.00022955 | 0.0061589 | 0.012925 | 2.4586e-21 | 0.001423 | 0.0015548 | 0.0017795 | 0.0037508 | 0.0041394 | 0.0040268 | 0.088988 | 0.097844 | 0.095062 | 0.0011423 | 0.00070004 | 0.0064149 | 0.0006997 | 0.0036722 | 0.0043483 | 0.015939 | 0.065805 | 0.10356
1 | 1.1 | All | Standard Deviation | 0.10806 | 0.074343 | 0.010864 | 0.048791 | 0.085099 | 0.11863 | 0.19674 | 0 | 0.21963 | 0 | 0.061011 | 0 | 0.10793 | 0.037568 | 0.11959 | 0 | 0.33217 | 0.0080843 | 9.5574e-05 | 0.022025 | 0.00014832 | 0.037834 | 4.0835e-05 | 0.038218 | 0.037032 | 0.025842 | 0.046285 | 0.055335 | 0.00026401 | 0.083585 | 0.0081314 | 0.027355 | 0.038883 | 7.164e-05 | 0.030319 | 0.00011189 | 0.07507 | 0.00028638 | 0.067508 | 0.026125 | 0.022009 | 0.028081 | 0.00018776 | 0.0022979 | 0.0011349 | 2.0108e-21 | 2.4795e-20 | 1.2155e-20 | 0.0043774 | 0.0048981 | 0.0069014 | 0.00013498 | 0.00016277 | 3.0771e-05 | 0.0034379 | 0.0040391 | 0.00097256 | 0.0024358 | 0.0017542 | 0.00035361 | 0.00017741 | 5.8958e-05 | 0.00013574 | 0.0033708 | 0.0010913 | 0.002542
1 | 1.2 | All | Standard Deviation | 0.8643 | 0.85987 | 0.98138 | 0.027825 | 0.12784 | 0.11754 | 0.089392 | 0 | 0.15637 | 0 | 0.096475 | 0 | 0.17541 | 0.013068 | 0.09996 | 0 | 0.16327 | 0.018057 | 0.0016589 | 0.11527 | 0.00054785 | 0.12134 | 0.00043304 | 0.11703 | 0.46556 | 0.16423 | 0.26722 | 0.038011 | 0.0025005 | 0.039866 | 0.018729 | 0.044808 | 0.010821 | 0.0029644 | 0.061236 | 0.0035442 | 0.08162 | 0.0028855 | 0.025579 | 0.37077 | 0.49408 | 0.14304 | 0.00081456 | 0.0094645 | 0.00070497 | 8.7237e-21 | 1.0216e-19 | 7.5507e-21 | 0.0078779 | 0.0087522 | 0.010484 | 0.020175 | 0.019001 | 0.016669 | 0.47818 | 0.44705 | 0.3901 | 0.0068116 | 0.0018585 | 0.0012427 | 0.0031036 | 0.0030489 | 0.017933 | 0.083713 | 0.048408 | 0.32488
1 | 1.3 | All | Standard Deviation | 1.2576 | 0.95465 | 0.48537 | 0.35192 | 1.3922 | 1.7173 | 0.11036 | 0 | 0.25488 | 0 | 0.1695 | 0 | 0.2595 | 0.00073941 | 0.10834 | 0 | 0.1602 | 0.027041 | 0.0086857 | 0.31124 | 0.0072538 | 0.34556 | 0.012154 | 0.28385 | 0.86409 | 0.20671 | 0.60663 | 0.06829 | 0.0033275 | 0.04159 | 0.029964 | 0.068555 | 0.00116 | 0.0043196 | 0.10322 | 0.03577 | 0.32578 | 0.030131 | 0.33409 | 0.61309 | 0.51574 | 0.14631 | 0.00016833 | 0.0014007 | 0.0006141 | 0.0016159 | 0.013363 | 0.0060355 | 0.00094476 | 0.0025932 | 0.0010996 | 0.0014379 | 0.001694 | 0.0031461 | 0.033851 | 0.037739 | 0.074586 | 0.00088171 | 0.00098092 | 0.014106 | 0.00039715 | 0.015498 | 0.0028929 | 0.0058027 | 0.28149 | 0.10763
1 | 1.4 | All | Standard Deviation | 1.03 | 0.59123 | 0.22563 | 0.53934 | 0.48063 | 0.83617 | 0.089303 | 0 | 0.17657 | 0 | 0.082982 | 0 | 0.079663 | 0.02654 | 0.042371 | 0 | 0.11142 | 0.031369 | 0.0024333 | 0.016396 | 0.00077497 | 0.026251 | 0.00091092 | 0.04563 | 0.50483 | 0.38534 | 0.20032 | 0.049944 | 0.0015024 | 0.036937 | 0.032646 | 0.061004 | 0.027525 | 0.0084441 | 0.05342 | 0.0042304 | 0.028181 | 0.0078351 | 0.026331 | 0.57361 | 0.18608 | 0.5087 | 0.00070525 | 0.0001897 | 0.0010792 | 0.012051 | 0.0032135 | 0.018578 | 0.0017711 | 0.0022703 | 0.0028678 | 0.0031653 | 0.0043008 | 0.0012171 | 0.074413 | 0.10091 | 0.026837 | 0.0021292 | 0.002106 | 0.0021871 | 0.00081867 | 0.0034452 | 0.0003696 | 0.018941 | 0.065248 | 0.004991
2 | 2.1 | All | Standard Deviation | 0.10255 | 0.011595 | 0.0040495 | 0.114 | 0.015569 | 0.098505 | 0.21479 | 0 | 0.40315 | 0 | 0.27168 | 0 | 0.50773 | 0.015113 | 0.27798 | 0 | 0.41394 | 0.016503 | 0.00037194 | 0.012083 | 0.00054531 | 0.035656 | 0.00036251 | 0.020263 | 0.057005 | 0.034553 | 0.013301 | 0.10164 | 0.00050007 | 0.10436 | 0.014654 | 0.12792 | 0.011778 | 0.00021617 | 0.063247 | 0.0013839 | 0.25372 | 0.0010499 | 0.10912 | 0.0033854 | 0.0087954 | 0.0063155 | 0.00010411 | 0.00030561 | 0.00081786 | 1.115e-21 | 3.2973e-21 | 8.7587e-21 | 0.0023162 | 0.0030142 | 0.0052264 | 0.00017587 | 0.00017047 | 5.6198e-05 | 0.004196 | 0.0040946 | 0.0014669 | 0.0018911 | 0.0011902 | 0.00039309 | 1.0406e-05 | 6.5164e-05 | 1.1531e-05 | 0.00019696 | 0.0012113 | 0.00021395
2 | 2.2 | All | Standard Deviation | 0.73695 | 1.5403 | 2.0202 | 1.1112 | 3.5598 | 2.6277 | 0.071189 | 0 | 0.09346 | 0 | 0.094989 | 0 | 0.25223 | 0.033667 | 0.15837 | 0 | 0.21267 | 0.017125 | 0.0023004 | 0.22311 | 0.0067077 | 0.21475 | 0.0090153 | 0.14901 | 0.43581 | 0.44646 | 0.4252 | 0.013981 | 0.0039664 | 0.052077 | 0.017147 | 0.029302 | 0.029438 | 0.0059356 | 0.16699 | 0.0044777 | 0.040262 | 0.034666 | 0.24194 | 1.2444 | 0.47369 | 0.78062 | 0.00050469 | 0.00096527 | 0.00036614 | 0.012158 | 1.0415e-20 | 0.0085049 | 0.012337 | 0.013245 | 0.017463 | 0.027413 | 0.026552 | 0.030826 | 0.64894 | 0.62461 | 0.72547 | 0.0055973 | 0.0034159 | 0.0063548 | 0.00082935 | 0.00054734 | 0.00041071 | 0.035287 | 0.01615 | 0.027083
2 | 2.3 | All | Standard Deviation | 0.972 | 0.45981 | 0.46927 | 0.51302 | 0.133 | 0.52866 | 0.08453 | 0 | 0.057934 | 0 | 0.013514 | 0 | 0.046416 | 0.0084659 | 0.057597 | 0 | 0.16254 | 0.016235 | 0.0019527 | 0.032882 | 0.0017022 | 0.036484 | 0.001283 | 0.078154 | 0.32219 | 0.038174 | 0.61537 | 0.016741 | 0.00040061 | 0.053205 | 0.016285 | 0.021346 | 0.0090475 | 0.0020525 | 0.015734 | 0.0083771 | 0.040334 | 0.0078439 | 0.035548 | 0.17953 | 0.66878 | 0.23963 | 0.00024228 | 0.0032295 | 0.0026267 | 0.0023258 | 0.054707 | 0.061019 | 0.0036344 | 0.0040923 | 0.0064768 | 0.0067973 | 0.0059423 | 0.0065972 | 0.16007 | 0.13834 | 0.15194 | 0.00066044 | 0.0042459 | 0.0018682 | 0.00021666 | 0.0050972 | 0.0018045 | 0.0040889 | 0.081423 | 0.038938
2 | 2.4 | All | Standard Deviation | 0.6419 | 0.76336 | 0.58033 | 0.185 | 1.3201 | 1.1716 | 0.017827 | 0 | 0.014509 | 0 | 0.014714 | 0 | 0.038651 | 0.017328 | 0.035274 | 0 | 0.060281 | 0.01733 | 0.0018757 | 0.058244 | 0.0018896 | 0.029518 | 0.002001 | 0.059208 | 0.46228 | 0.48792 | 0.43053 | 0.0087535 | 0.00059221 | 0.015214 | 0.017563 | 0.010703 | 0.016458 | 0.0070654 | 0.078405 | 0.0073772 | 0.045974 | 0.0012439 | 0.047763 | 1.1697 | 0.47399 | 0.047533 | 0.00051413 | 0.001082 | 0.0011576 | 0.012386 | 0.018332 | 1.2398e-20 | 0.0044102 | 0.0045343 | 0.0051447 | 0.012422 | 0.011633 | 0.0060682 | 0.2951 | 0.27498 | 0.14064 | 0.0017099 | 0.0020715 | 0.0019743 | 0.00098804 | 0.006253 | 0.0031607 | 0.023811 | 0.10673 | 0.063863
1 | 1.1 | 1.1.1 | Mean | 101.9406 | 50.405 | 2.7975 | 51.5355 | 47.6076 | 99.1431 | 281.8003 | -30 | 488.4611 | 0 | 282.0499 | -150 | 488.2199 | -120.0717 | 281.661 | 90 | 487.8188 | 119.9823 | 0.29151 | -96.54 | 0.35841 | 146.8337 | 0.34377 | 16.7087 | 31.7707 | 43.638 | 26.5318 | 122.7834 | -0.0018957 | 122.7153 | 120.0367 | 122.7576 | -120.0424 | 0.32953 | -50.7297 | 0.1409 | 49.9694 | 0.37896 | 173.9265 | 25.6119 | 5.8945 | 18.8986 | 48.1926 | 48.5588 | 48.196 | 2.5806e-16 | 2.62e-16 | 2.581e-16 | 24.2421 | 24.1924 | 24.1768 | 0.040342 | 0.021259 | 0.041399 | 0.97797 | 0.51431 | 1.0009 | 18.964 | 18.6105 | 18.7038 | 0.0023092 | 0.0033996 | 0.010544 | 0.043792 | 0.063267 | 0.19721
1 | 1.1 | 1.1.2 | Mean | 101.8094 | 50.2762 | 2.8144 | 51.5332 | 47.4617 | 98.995 | 281.8135 | -30 | 488.5202 | 0 | 282.1217 | -150 | 488.3734 | -120.0537 | 281.7287 | 90 | 487.8707 | 119.979 | 0.29156 | -96.5788 | 0.35856 | 146.813 | 0.34385 | 16.662 | 31.7354 | 43.5982 | 26.4757 | 122.7987 | -0.0016699 | 122.7288 | 120.0344 | 122.7966 | -120.0242 | 0.32944 | -50.7895 | 0.1408 | 49.8292 | 0.37858 | 173.896 | 25.5754 | 5.8517 | 18.849 | 48.1923 | 48.5559 | 48.1949 | 2.5806e-16 | 2.6196e-16 | 2.5808e-16 | 24.2466 | 24.1972 | 24.1832 | 0.040557 | 0.021495 | 0.041382 | 0.98336 | 0.52012 | 1.0008 | 18.9664 | 18.6086 | 18.7035 | 0.0025227 | 0.0034888 | 0.010555 | 0.047847 | 0.064921 | 0.19742
1 | 1.1 | 1.1.3 | Mean | 101.7262 | 50.2763 | 2.8177 | 51.4499 | 47.4586 | 98.9085 | 281.4664 | -30 | 488.1137 | 0 | 282.0004 | -150 | 488.1653 | -120.1259 | 281.4962 | 90 | 487.2712 | 119.9669 | 0.29137 | -96.5774 | 0.3587 | 146.7603 | 0.34381 | 16.633 | 31.6967 | 43.5895 | 26.44 | 122.6962 | -0.0013695 | 122.5778 | 120.0216 | 122.7439 | -120.0988 | 0.32939 | -50.7684 | 0.14102 | 49.8526 | 0.37913 | 173.7974 | 25.5613 | 5.8641 | 18.8509 | 48.1923 | 48.5542 | 48.1937 | 2.5806e-16 | 2.6195e-16 | 2.5807e-16 | 24.2509 | 24.2022 | 24.1906 | 0.040591 | 0.021572 | 0.041442 | 0.98437 | 0.52208 | 1.0025 | 18.9689 | 18.607 | 18.7031 | 0.0026614 | 0.0035109 | 0.010315 | 0.050484 | 0.065328 | 0.19292
1 | 1.2 | 1.2.1 | Mean | 459.7302 | 402.4464 | 298.0931 | 57.2838 | 104.3533 | 161.6371 | 281.6578 | -30 | 488.2442 | 0 | 281.9163 | -150 | 487.9438 | -120.0633 | 281.4842 | 90 | 487.5272 | 120.0149 | 0.74972 | -58.3833 | 0.7812 | -178.7499 | 0.72208 | 56.2256 | 151.2227 | 167.4263 | 141.0812 | 122.303 | -0.13567 | 122.217 | 119.938 | 122.2114 | -120.1406 | 2.0841 | -55.6289 | 1.9039 | 61.7537 | 1.8214 | -172.6818 | 144.3991 | 122.6685 | 135.3788 | 48.1944 | 48.5806 | 48.1988 | 2.5808e-16 | 2.6223e-16 | 2.5812e-16 | 24.1573 | 24.0765 | 24.1054 | 1.1434 | 1.1687 | 1.1293 | 27.6206 | 28.1391 | 27.2219 | 18.2937 | 18.2019 | 18.2468 | 3.9741 | 3.9115 | 3.9028 | 72.7005 | 71.1969 | 71.2141
1 | 1.2 | 1.2.2 | Mean | 461.077 | 403.8199 | 299.6082 | 57.2571 | 104.2117 | 161.4687 | 281.6429 | -30 | 488.2418 | 0 | 281.9275 | -150 | 487.9617 | -120.0786 | 281.481 | 90 | 487.5 | 120.0236 | 0.75002 | -58.1766 | 0.78074 | -178.6157 | 0.72154 | 56.4586 | 151.8241 | 167.7521 | 141.5008 | 122.3003 | -0.13129 | 122.208 | 119.9506 | 122.2163 | -120.1549 | 2.0855 | -55.5071 | 1.9064 | 61.9144 | 1.8212 | -172.6346 | 144.9212 | 123.3368 | 135.562 | 48.1933 | 48.5682 | 48.1974 | 2.5807e-16 | 2.621e-16 | 2.5811e-16 | 24.1486 | 24.067 | 24.0954 | 1.1705 | 1.1938 | 1.1524 | 28.2655 | 28.7323 | 27.7672 | 18.2852 | 18.199 | 18.2453 | 3.9698 | 3.9169 | 3.8898 | 72.5883 | 71.2846 | 70.9705
1 | 1.2 | 1.2.3 | Mean | 461.342 | 404.0293 | 299.9312 | 57.3127 | 104.0981 | 161.4108 | 281.8046 | -30 | 488.5139 | 0 | 282.0887 | -150 | 488.2561 | -120.0893 | 281.6557 | 90 | 487.7954 | 119.9889 | 0.75273 | -58.3684 | 0.78183 | -178.8579 | 0.7224 | 56.3231 | 152.139 | 167.6253 | 141.5777 | 122.3675 | -0.13139 | 122.2811 | 119.9138 | 122.2913 | -120.1618 | 2.0898 | -55.5573 | 1.9109 | 61.859 | 1.8163 | -172.6412 | 145.1162 | 123.6331 | 135.2801 | 48.1928 | 48.562 | 48.1977 | 2.5806e-16 | 2.6203e-16 | 2.5811e-16 | 24.1416 | 24.059 | 24.0845 | 1.1828 | 1.206 | 1.1617 | 28.5547 | 29.0151 | 27.9778 | 18.2802 | 18.1984 | 18.2477 | 3.9681 | 3.9166 | 3.8674 | 72.5368 | 71.2762 | 70.5707
1 | 1.3 | 1.3.1 | Mean | 1256.0543 | 1173.1604 | 996.8497 | 82.8938 | 176.3108 | 259.2046 | 281.4091 | -30 | 487.6129 | 0 | 281.5483 | -150 | 487.5011 | -120.0499 | 281.3445 | 90 | 487.2909 | 119.9858 | 1.7229 | -46.2964 | 1.8256 | -167.0665 | 1.7491 | 68.4737 | 409.9693 | 444.1052 | 401.9798 | 121.0866 | -0.29249 | 121.1314 | 119.7789 | 120.8834 | -120.2354 | 3.769 | -27.1178 | 4.553 | 72.1551 | 4.8867 | -168.3776 | 407.2683 | 371.7166 | 394.1755 | 48.1911 | 48.3695 | 48.2079 | 231.3133 | 230.7309 | 236.9018 | 24.1549 | 24.0774 | 24.1019 | 1.1565 | 1.1745 | 1.1353 | 27.9361 | 28.2788 | 27.3639 | 18.2911 | 18.2053 | 18.2424 | 3.9735 | 3.8654 | 3.9071 | 72.6789 | 70.371 | 71.2751
1 | 1.3 | 1.3.2 | Mean | 1255.0324 | 1172.1108 | 996.8835 | 82.9215 | 175.2274 | 258.1489 | 281.6223 | -30 | 488.1226 | 0 | 281.8846 | -150 | 488.016 | -120.0488 | 281.5607 | 90 | 487.5926 | 119.9823 | 1.7193 | -46.3676 | 1.8255 | -167.1118 | 1.7497 | 68.3363 | 409.1466 | 444.1411 | 401.7447 | 121.2231 | -0.29114 | 121.212 | 119.7742 | 121.0203 | -120.2331 | 3.7632 | -27.3178 | 4.5522 | 72.0743 | 4.8895 | -168.4364 | 406.3708 | 371.3586 | 394.3815 | 48.1909 | 48.3669 | 48.2071 | 231.3114 | 230.7057 | 236.8929 | 24.1551 | 24.078 | 24.1033 | 1.158 | 1.174 | 1.1311 | 27.9706 | 28.2666 | 27.2627 | 18.2919 | 18.2072 | 18.2528 | 3.9738 | 3.8675 | 3.91 | 72.6881 | 70.4162 | 71.3691
1 | 1.3 | 1.3.3 | Mean | 1253.553 | 1171.2544 | 997.7067 | 82.2986 | 173.5477 | 255.8463 | 281.4661 | -30 | 487.8607 | 0 | 281.7534 | -150 | 487.8148 | -120.0484 | 281.4396 | 90 | 487.3482 | 119.9373 | 1.7064 | -45.7965 | 1.813 | -166.4919 | 1.7284 | 68.882 | 408.2418 | 444.4798 | 400.8314 | 121.1583 | -0.29745 | 121.1537 | 119.7248 | 120.9581 | -120.2341 | 3.7606 | -27.262 | 4.4907 | 72.6746 | 4.836 | -167.8306 | 406.096 | 370.6999 | 394.4585 | 48.1908 | 48.3674 | 48.2068 | 231.31 | 230.7106 | 236.8902 | 24.1534 | 24.0732 | 24.1011 | 1.1594 | 1.1771 | 1.1372 | 28.0038 | 28.3372 | 27.4082 | 18.2929 | 18.2058 | 18.2703 | 3.973 | 3.8932 | 3.9129 | 72.6774 | 70.8796 | 71.4898
1 | 1.4 | 1.4.1 | Mean | 1870.0157 | 1749.9783 | 1529.1942 | 120.0374 | 220.7841 | 340.8215 | 281.4151 | -30 | 487.7409 | 0 | 281.6564 | -150 | 487.6298 | -120.0592 | 281.3509 | 90 | 487.2423 | 119.9873 | 2.5186 | -44.1503 | 2.6185 | -164.0994 | 2.6054 | 70.9138 | 611.2369 | 652.079 | 606.6998 | 120.3322 | -0.41167 | 120.3439 | 119.6643 | 120.1356 | -120.349 | 5.3077 | -20.0423 | 6.9879 | 71.4466 | 7.2847 | -168.1288 | 601.5649 | 560.3277 | 588.0857 | 48.1872 | 47.7721 | 48.1986 | 411.7028 | 404.6401 | 414.8397 | 24.1568 | 24.0802 | 24.1064 | 1.158 | 1.174 | 1.1358 | 27.9735 | 28.2708 | 27.3811 | 18.2939 | 18.1982 | 18.2442 | 3.973 | 3.8709 | 3.9059 | 72.6816 | 70.4436 | 71.261
1 | 1.4 | 1.4.2 | Mean | 1870.5569 | 1749.8147 | 1529.4997 | 120.7422 | 220.315 | 341.0572 | 281.2526 | -30 | 487.3906 | 0 | 281.4904 | -150 | 487.4742 | -120.0606 | 281.3009 | 90 | 487.093 | 119.9737 | 2.5219 | -44.1183 | 2.6174 | -164.0559 | 2.6038 | 71.0049 | 611.7392 | 651.9326 | 606.885 | 120.2351 | -0.41178 | 120.2962 | 119.6459 | 120.0369 | -120.3529 | 5.3193 | -20.0742 | 6.9946 | 71.4125 | 7.2712 | -168.0835 | 602.271 | 560.4726 | 587.0711 | 48.186 | 47.772 | 48.1991 | 411.683 | 404.6391 | 414.8487 | 24.1554 | 24.0783 | 24.1041 | 1.1611 | 1.1788 | 1.138 | 28.0478 | 28.3824 | 27.4302 | 18.2921 | 18.2004 | 18.2419 | 3.9714 | 3.8775 | 3.9059 | 72.6449 | 70.5725 | 71.2511
1 | 1.4 | 1.4.3 | Mean | 1872.0077 | 1750.9107 | 1529.6345 | 121.097 | 221.2762 | 342.3732 | 281.2696 | -30 | 487.5275 | 0 | 281.5748 | -150 | 487.5223 | -120.1059 | 281.2666 | 90 | 487.0243 | 119.9275 | 2.5234 | -44.1279 | 2.6189 | -164.1032 | 2.6039 | 70.9551 | 612.2466 | 652.6611 | 607.1001 | 120.2636 | -0.41432 | 120.2712 | 119.6008 | 120.0241 | -120.3985 | 5.3241 | -20.1466 | 6.9957 | 71.3907 | 7.271 | -168.0828 | 602.701 | 560.6971 | 587.5127 | 48.1873 | 47.7717 | 48.2006 | 411.7049 | 404.6341 | 414.8755 | 24.1533 | 24.0757 | 24.1007 | 1.1643 | 1.1826 | 1.1379 | 28.1223 | 28.4723 | 27.4244 | 18.2897 | 18.2025 | 18.2399 | 3.9725 | 3.8726 | 3.9066 | 72.6552 | 70.4907 | 71.2553
2 | 2.1 | 2.1.1 | Mean | 101.7149 | 50.2823 | 2.815 | 51.4327 | 47.4672 | 98.8999 | 281.5226 | -30 | 488.1526 | 0 | 281.985 | -150 | 488.1314 | -120.0848 | 281.5104 | 90 | 487.3614 | 119.9803 | 0.2918 | -96.601 | 0.35898 | 146.7548 | 0.34411 | 16.6338 | 31.715 | 43.5613 | 26.4387 | 122.706 | -0.00152 | 122.6005 | 120.0363 | 122.7355 | -120.0613 | 0.32921 | -50.7654 | 0.14104 | 49.9017 | 0.37938 | 173.8264 | 25.551 | 5.8759 | 18.8554 | 48.1922 | 48.553 | 48.1927 | 2.5805e-16 | 2.6193e-16 | 2.5806e-16 | 24.2552 | 24.2077 | 24.1994 | 0.04052 | 0.021638 | 0.041282 | 0.98282 | 0.52379 | 0.99901 | 18.9718 | 18.6052 | 18.7026 | 0.0026813 | 0.0035094 | 0.010332 | 0.050869 | 0.065294 | 0.19324
2 | 2.1 | 2.1.2 | Mean | 101.5574 | 50.3023 | 2.8091 | 51.2551 | 47.4932 | 98.7483 | 281.1864 | -30 | 487.469 | 0 | 281.5291 | -150 | 487.3369 | -120.0701 | 281.1101 | 90 | 486.7743 | 119.9555 | 0.29122 | -96.59 | 0.3581 | 146.8246 | 0.34357 | 16.647 | 31.6208 | 43.5062 | 26.4304 | 122.5336 | -0.0013723 | 122.4522 | 120.0147 | 122.5352 | -120.0451 | 0.32892 | -50.6664 | 0.13878 | 50.2875 | 0.37741 | 174.0327 | 25.5468 | 5.8883 | 18.8672 | 48.1922 | 48.5524 | 48.1922 | 2.5805e-16 | 2.6193e-16 | 2.5805e-16 | 24.2578 | 24.2111 | 24.2052 | 0.040557 | 0.021298 | 0.041225 | 0.98383 | 0.51564 | 0.99787 | 18.9739 | 18.6038 | 18.7022 | 0.0026629 | 0.0036326 | 0.010355 | 0.050526 | 0.06758 | 0.19367
2 | 2.1 | 2.1.3 | Mean | 101.5224 | 50.3024 | 2.8073 | 51.2201 | 47.4951 | 98.7152 | 281.1229 | -30 | 487.4405 | 0 | 281.501 | -150 | 487.1865 | -120.1003 | 280.9761 | 90 | 486.5624 | 119.9868 | 0.2911 | -96.5768 | 0.35799 | 146.8024 | 0.34341 | 16.6736 | 31.6122 | 43.4975 | 26.4127 | 122.5265 | -0.00058946 | 122.3992 | 120.0426 | 122.4975 | -120.0681 | 0.32878 | -50.6477 | 0.13853 | 50.38 | 0.37776 | 173.9914 | 25.5442 | 5.8929 | 18.8652 | 48.1924 | 48.5526 | 48.1911 | 2.5806e-16 | 2.6193e-16 | 2.5804e-16 | 24.2598 | 24.2137 | 24.2098 | 0.040236 | 0.021491 | 0.041338 | 0.97611 | 0.52037 | 1.0008 | 18.9756 | 18.6028 | 18.7018 | 0.0026806 | 0.0035341 | 0.010342 | 0.050865 | 0.065743 | 0.19341
2 | 2.2 | 2.2.1 | Mean | 1772.9316 | 1652.6697 | 1434.2713 | 120.2618 | 218.3985 | 338.6603 | 281.4451 | -30 | 487.7195 | 0 | 281.5829 | -150 | 487.4702 | -120.0777 | 281.3011 | 90 | 487.2608 | 120.0098 | 1.863 | -19.3414 | 3.2922 | -162.2482 | 2.4552 | 52.6902 | 480.3333 | 833.6586 | 458.9397 | 119.5944 | -0.48128 | 122.2908 | 119.9367 | 119.4345 | -120.5258 | 6.8339 | -15.9399 | 1.8847 | 61.7452 | 9.0575 | -167.112 | 787.7228 | 121.4836 | 743.4634 | 48.1805 | 48.5534 | 48.1983 | 580.3404 | 2.6194e-16 | 559.7777 | 24.1893 | 24.1147 | 24.165 | 1.0999 | 1.1303 | 1.0739 | 26.6051 | 27.2572 | 25.952 | 18.3024 | 18.1762 | 18.2277 | 3.9716 | 3.8779 | 3.9041 | 72.6902 | 70.486 | 71.1625
2 | 2.2 | 2.2.2 | Mean | 1771.5171 | 1651.063 | 1436.5104 | 120.4541 | 214.5525 | 335.0066 | 281.3656 | -30 | 487.6757 | 0 | 281.5757 | -150 | 487.395 | -120.0144 | 281.2034 | 90 | 487.0605 | 120.0177 | 1.8635 | -19.4308 | 3.285 | -162.0528 | 2.4478 | 52.8059 | 479.8561 | 832.9259 | 458.7352 | 119.5701 | -0.48902 | 122.2362 | 119.938 | 119.3822 | -120.4715 | 6.8326 | -16.1696 | 1.8904 | 61.819 | 9.0274 | -166.9272 | 786.572 | 122.0408 | 742.4501 | 48.1812 | 48.5528 | 48.199 | 580.3579 | 2.6193e-16 | 559.7946 | 24.1782 | 24.1031 | 24.1495 | 1.1292 | 1.1533 | 1.1108 | 27.3017 | 27.7977 | 26.8255 | 18.3018 | 18.1809 | 18.24 | 3.9726 | 3.8787 | 3.904 | 72.7063 | 70.518 | 71.2088
2 | 2.2 | 2.2.3 | Mean | 1771.8656 | 1649.5901 | 1438.3035 | 122.2754 | 211.2867 | 333.5621 | 281.5076 | -30 | 487.855 | 0 | 281.7437 | -150 | 487.8646 | -120.0262 | 281.5132 | 90 | 487.4856 | 119.9849 | 1.8593 | -19.7647 | 3.2984 | -162.4817 | 2.4657 | 52.5102 | 479.463 | 832.8503 | 459.5523 | 119.5943 | -0.48366 | 122.3403 | 119.9077 | 119.4312 | -120.479 | 6.823 | -16.2647 | 1.8936 | 61.81 | 9.0965 | -167.4069 | 785.2364 | 122.4257 | 741.9281 | 48.1815 | 48.5547 | 48.1988 | 580.3638 | 2.6195e-16 | 559.788 | 24.1647 | 24.0883 | 24.1302 | 1.1547 | 1.1833 | 1.1352 | 27.9018 | 28.5028 | 27.3921 | 18.2924 | 18.1828 | 18.2368 | 3.971 | 3.8776 | 3.9047 | 72.6387 | 70.5061 | 71.2101
2 | 2.3 | 2.3.1 | Mean | 1838.1807 | 1708.9126 | 1493.1103 | 129.2681 | 215.8022 | 345.0703 | 281.5665 | -30 | 487.8897 | 0 | 281.7055 | -150 | 487.7645 | -120.0507 | 281.4942 | 90 | 487.5539 | 119.9648 | 2.2773 | -52.3557 | 2.7489 | -162.5812 | 2.9727 | 69.418 | 509.6221 | 635.0708 | 693.4878 | 121.255 | -0.27668 | 120.4915 | 119.6122 | 119.4243 | -120.441 | 3.7552 | -27.0009 | 6.9928 | 71.2602 | 9.1246 | -167.5046 | 406.6937 | 559.9333 | 742.2856 | 48.1906 | 47.7676 | 48.2003 | 231.3086 | 404.5641 | 559.8235 | 24.1644 | 24.0895 | 24.1248 | 1.1412 | 1.1689 | 1.1219 | 27.5769 | 28.1582 | 27.0658 | 18.2957 | 18.185 | 18.2445 | 3.9717 | 3.8811 | 3.9119 | 72.665 | 70.577 | 71.3712
2 | 2.3 | 2.3.2 | Mean | 1839.4328 | 1709.5352 | 1493.5246 | 129.8977 | 216.0106 | 345.9083 | 281.3977 | -30 | 487.7768 | 0 | 281.7269 | -150 | 487.7725 | -120.0672 | 281.3952 | 90 | 487.2324 | 119.9956 | 2.2807 | -52.4192 | 2.7472 | -162.5586 | 2.9738 | 69.5189 | 509.9856 | 635.1352 | 694.312 | 121.2237 | -0.27645 | 120.3869 | 119.6428 | 119.392 | -120.4588 | 3.7534 | -26.9794 | 7.0089 | 71.3134 | 9.1181 | -167.4847 | 406.47 | 560.9818 | 742.0833 | 48.1902 | 47.7724 | 48.2037 | 231.304 | 404.646 | 559.9032 | 24.1604 | 24.085 | 24.1183 | 1.1495 | 1.1762 | 1.1262 | 27.7716 | 28.33 | 27.1625 | 18.2955 | 18.1895 | 18.241 | 3.9721 | 3.8712 | 3.9099 | 72.672 | 70.4154 | 71.3199
2 | 2.3 | 2.3.3 | Mean | 1840.0946 | 1709.81 | 1494.0468 | 130.2845 | 215.7632 | 346.0477 | 281.4739 | -30 | 487.8108 | 0 | 281.7305 | -150 | 487.8486 | -120.0554 | 281.4957 | 90 | 487.4346 | 119.9891 | 2.2806 | -52.4025 | 2.7455 | -162.5098 | 2.9713 | 69.5719 | 510.2647 | 635.1385 | 694.6914 | 121.2291 | -0.27723 | 120.4221 | 119.6372 | 119.384 | -120.447 | 3.7575 | -27.01 | 7.0049 | 71.3393 | 9.109 | -167.4355 | 406.8251 | 561.1767 | 741.8082 | 48.1905 | 47.7737 | 48.2054 | 231.307 | 404.6679 | 559.9434 | 24.1571 | 24.0813 | 24.1118 | 1.1547 | 1.1807 | 1.1349 | 27.8943 | 28.4319 | 27.3636 | 18.2945 | 18.1935 | 18.2418 | 3.972 | 3.8739 | 3.9083 | 72.6649 | 70.4789 | 71.2948
2 | 2.4 | 2.4.1 | Mean | 1584.6134 | 1483.1614 | 1282.4132 | 101.452 | 200.7481 | 302.2002 | 281.2812 | -30 | 487.4988 | 0 | 281.5805 | -150 | 487.6196 | -120.0652 | 281.351 | 90 | 487.1313 | 119.9495 | 2.8063 | -38.0392 | 2.0306 | -177.2606 | 1.7962 | 74.8449 | 708.6076 | 501.1438 | 374.8621 | 119.4589 | -0.5644 | 120.3227 | 119.6688 | 122.2648 | -120.1501 | 6.846 | -16.2522 | 6.981 | 71.5168 | 1.8181 | -172.6189 | 787.3467 | 560.3943 | 135.4204 | 48.1832 | 47.778 | 48.199 | 580.4058 | 404.7412 | 2.5813e-16 | 24.1647 | 24.0879 | 24.1159 | 1.1416 | 1.1586 | 1.1226 | 27.5853 | 27.9092 | 27.0727 | 18.2962 | 18.1926 | 18.2477 | 3.9738 | 3.8803 | 3.9128 | 72.706 | 70.5935 | 71.3996
2 | 2.4 | 2.4.2 | Mean | 1583.3966 | 1481.8396 | 1283.132 | 101.557 | 198.7075 | 300.2645 | 281.3168 | -30 | 487.5042 | 0 | 281.5848 | -150 | 487.6851 | -120.0384 | 281.4213 | 90 | 487.2513 | 119.9833 | 2.8026 | -38.0434 | 2.0276 | -177.2126 | 1.7943 | 74.9601 | 707.8537 | 500.4742 | 375.0687 | 119.4486 | -0.56543 | 120.3418 | 119.7036 | 122.2814 | -120.1257 | 6.8361 | -16.3482 | 6.9741 | 71.6086 | 1.8175 | -172.556 | 785.7819 | 560.5511 | 135.5066 | 48.1841 | 47.7799 | 48.1969 | 580.4266 | 404.773 | 2.581e-16 | 24.1601 | 24.0831 | 24.1112 | 1.1577 | 1.1749 | 1.1303 | 27.9695 | 28.2952 | 27.2521 | 18.2946 | 18.1959 | 18.2491 | 3.972 | 3.868 | 3.9107 | 72.6665 | 70.3817 | 71.3675
2 | 2.4 | 2.4.3 | Mean | 1583.6506 | 1481.8388 | 1283.5618 | 101.8118 | 198.277 | 300.0887 | 281.2976 | -30 | 487.5262 | 0 | 281.6079 | -150 | 487.6878 | -120.0708 | 281.391 | 90 | 487.1808 | 119.9594 | 2.8038 | -38.1421 | 2.0271 | -177.2664 | 1.7983 | 74.8787 | 707.767 | 500.1942 | 375.6893 | 119.4415 | -0.56541 | 120.3117 | 119.6819 | 122.2848 | -120.157 | 6.8322 | -16.4075 | 6.9889 | 71.5582 | 1.8199 | -172.6497 | 785.0583 | 561.2824 | 135.4982 | 48.1841 | 47.7799 | 48.197 | 580.4279 | 404.7729 | 2.5811e-16 | 24.1559 | 24.0788 | 24.1056 | 1.166 | 1.1812 | 1.1346 | 28.1654 | 28.4414 | 27.35 | 18.2928 | 18.1964 | 18.2452 | 3.9722 | 3.8724 | 3.9066 | 72.6632 | 70.4645 | 71.2765
1 | 1.1 | All | Mean | 101.8254 | 50.3192 | 2.8099 | 51.5062 | 47.5093 | 99.0155 | 281.6934 | -30 | 488.365 | 0 | 282.0573 | -150 | 488.2529 | -120.0837 | 281.6286 | 90 | 487.6536 | 119.9761 | 0.29148 | -96.5654 | 0.35855 | 146.8023 | 0.34381 | 16.6679 | 31.7343 | 43.6086 | 26.4825 | 122.7594 | -0.001645 | 122.6739 | 120.0309 | 122.766 | -120.0551 | 0.32945 | -50.7625 | 0.1409 | 49.8837 | 0.37889 | 173.8733 | 25.5828 | 5.8701 | 18.8662 | 48.1924 | 48.5563 | 48.1949 | 2.5806e-16 | 2.6197e-16 | 2.5808e-16 | 24.2465 | 24.1973 | 24.1836 | 0.040497 | 0.021442 | 0.041408 | 0.9819 | 0.51884 | 1.0014 | 18.9664 | 18.6087 | 18.7034 | 0.0024978 | 0.0034664 | 0.010471 | 0.047374 | 0.064505 | 0.19585
1 | 1.2 | All | Mean | 460.7164 | 403.4319 | 299.2109 | 57.2845 | 104.221 | 161.5055 | 281.7018 | -30 | 488.3333 | 0 | 281.9775 | -150 | 488.0539 | -120.0771 | 281.5403 | 90 | 487.6075 | 120.0091 | 0.75083 | -58.3094 | 0.78126 | -178.7412 | 0.72201 | 56.3358 | 151.7286 | 167.6012 | 141.3866 | 122.3236 | -0.13278 | 122.2353 | 119.9341 | 122.2397 | -120.1524 | 2.0865 | -55.5644 | 1.9071 | 61.8424 | 1.8196 | -172.6525 | 144.8122 | 123.2128 | 135.4069 | 48.1935 | 48.5702 | 48.198 | 2.5807e-16 | 2.6212e-16 | 2.5812e-16 | 24.1492 | 24.0675 | 24.0951 | 1.1655 | 1.1895 | 1.1478 | 28.1469 | 28.6288 | 27.6556 | 18.2864 | 18.1998 | 18.2466 | 3.9706 | 3.915 | 3.8867 | 72.6085 | 71.2526 | 70.9184
1 | 1.3 | All | Mean | 1254.8799 | 1172.1752 | 997.1466 | 82.7047 | 175.0286 | 257.7332 | 281.4992 | -30 | 487.8654 | 0 | 281.7288 | -150 | 487.7773 | -120.049 | 281.4483 | 90 | 487.4106 | 119.9685 | 1.7162 | -46.1535 | 1.8213 | -166.8901 | 1.7424 | 68.564 | 409.1193 | 444.242 | 401.5186 | 121.156 | -0.29369 | 121.1657 | 119.7593 | 120.9539 | -120.2342 | 3.7643 | -27.2325 | 4.532 | 72.3013 | 4.8707 | -168.2148 | 406.5783 | 371.2584 | 394.3385 | 48.191 | 48.3679 | 48.2073 | 231.3116 | 230.7157 | 236.895 | 24.1545 | 24.0762 | 24.1021 | 1.158 | 1.1752 | 1.1345 | 27.9701 | 28.2942 | 27.3449 | 18.292 | 18.2061 | 18.2552 | 3.9734 | 3.8754 | 3.91 | 72.6815 | 70.5556 | 71.378
1 | 1.4 | All | Mean | 1870.8601 | 1750.2346 | 1529.4428 | 120.6256 | 220.7918 | 341.4173 | 281.3125 | -30 | 487.553 | 0 | 281.5739 | -150 | 487.5421 | -120.0752 | 281.3061 | 90 | 487.1199 | 119.9628 | 2.5213 | -44.1322 | 2.6183 | -164.0862 | 2.6044 | 70.9579 | 611.7409 | 652.2242 | 606.895 | 120.277 | -0.41259 | 120.3038 | 119.637 | 120.0655 | -120.3668 | 5.317 | -20.0877 | 6.9927 | 71.4166 | 7.2757 | -168.0984 | 602.1789 | 560.4991 | 587.5565 | 48.1868 | 47.7719 | 48.1994 | 411.6969 | 404.6378 | 414.8546 | 24.1552 | 24.0781 | 24.1037 | 1.1612 | 1.1785 | 1.1372 | 28.0478 | 28.3751 | 27.4119 | 18.2919 | 18.2004 | 18.242 | 3.9723 | 3.8737 | 3.9061 | 72.6606 | 70.5023 | 71.2558
2 | 2.1 | All | Mean | 101.5983 | 50.2957 | 2.8105 | 51.3026 | 47.4852 | 98.7878 | 281.2773 | -30 | 487.6874 | 0 | 281.6717 | -150 | 487.5516 | -120.0851 | 281.1989 | 90 | 486.8993 | 119.9742 | 0.29137 | -96.5893 | 0.35836 | 146.794 | 0.3437 | 16.6515 | 31.6493 | 43.5217 | 26.4273 | 122.5887 | -0.0011606 | 122.484 | 120.0312 | 122.5894 | -120.0582 | 0.32897 | -50.6932 | 0.13945 | 50.1897 | 0.37818 | 173.9502 | 25.5473 | 5.8857 | 18.8626 | 48.1923 | 48.5527 | 48.192 | 2.5805e-16 | 2.6193e-16 | 2.5805e-16 | 24.2576 | 24.2108 | 24.2048 | 0.040438 | 0.021475 | 0.041282 | 0.98092 | 0.51994 | 0.99922 | 18.9738 | 18.6039 | 18.7022 | 0.0026749 | 0.0035587 | 0.010343 | 0.050754 | 0.066206 | 0.19344
2 | 2.2 | All | Mean | 1772.1047 | 1651.1076 | 1436.3617 | 120.9971 | 214.7459 | 335.743 | 281.4395 | -30 | 487.7501 | 0 | 281.6341 | -150 | 487.5766 | -120.0395 | 281.3393 | 90 | 487.269 | 120.0042 | 1.8619 | -19.5123 | 3.2919 | -162.2609 | 2.4562 | 52.6688 | 479.8841 | 833.1449 | 459.0757 | 119.5863 | -0.48466 | 122.2891 | 119.9275 | 119.4159 | -120.4921 | 6.8298 | -16.1247 | 1.8895 | 61.7914 | 9.0605 | -167.1487 | 786.5104 | 121.9834 | 742.6139 | 48.1811 | 48.5536 | 48.1987 | 580.354 | 2.6194e-16 | 559.7868 | 24.1774 | 24.102 | 24.1483 | 1.1279 | 1.1556 | 1.1066 | 27.2695 | 27.8526 | 26.7232 | 18.2989 | 18.18 | 18.2348 | 3.9717 | 3.8781 | 3.9043 | 72.6784 | 70.5034 | 71.1938
2 | 2.3 | All | Mean | 1839.236 | 1709.4192 | 1493.5606 | 129.8168 | 215.8587 | 345.6754 | 281.4793 | -30 | 487.8258 | 0 | 281.721 | -150 | 487.7952 | -120.0578 | 281.4617 | 90 | 487.407 | 119.9832 | 2.2795 | -52.3925 | 2.7472 | -162.5499 | 2.9726 | 69.503 | 509.9575 | 635.1148 | 694.1638 | 121.2359 | -0.27679 | 120.4335 | 119.6307 | 119.4001 | -120.4489 | 3.7553 | -26.9968 | 7.0022 | 71.3043 | 9.1172 | -167.4749 | 406.6629 | 560.6973 | 742.059 | 48.1904 | 47.7712 | 48.2031 | 231.3065 | 404.626 | 559.89 | 24.1606 | 24.0853 | 24.1183 | 1.1485 | 1.1753 | 1.1277 | 27.7476 | 28.3067 | 27.1973 | 18.2953 | 18.1893 | 18.2424 | 3.9719 | 3.8754 | 3.91 | 72.6673 | 70.4904 | 71.3286
2 | 2.4 | All | Mean | 1583.8868 | 1482.2799 | 1283.0357 | 101.6069 | 199.2442 | 300.8511 | 281.2985 | -30 | 487.5097 | 0 | 281.5911 | -150 | 487.6642 | -120.0581 | 281.3878 | 90 | 487.1878 | 119.9641 | 2.8043 | -38.0749 | 2.0284 | -177.2465 | 1.7962 | 74.8945 | 708.0761 | 500.6041 | 375.2067 | 119.4497 | -0.56508 | 120.3254 | 119.6848 | 122.277 | -120.1442 | 6.8381 | -16.336 | 6.9813 | 71.5612 | 1.8185 | -172.6082 | 786.0623 | 560.7426 | 135.475 | 48.1838 | 47.7793 | 48.1976 | 580.4201 | 404.7623 | 2.5811e-16 | 24.1602 | 24.0833 | 24.1109 | 1.1551 | 1.1716 | 1.1292 | 27.9067 | 28.2153 | 27.2249 | 18.2945 | 18.195 | 18.2473 | 3.9727 | 3.8736 | 3.91 | 72.6786 | 70.4799 | 71.3479
1 | 1.1 | All | Covariance | [66 empty] | 5.4939e-07 | 7.6354e-07 | 1.5489e-07 | 4.2855e-07 | -9.9294e-08 | 4.3372e-08
1 | 1.2 | All | Covariance | [66 empty] | -0.00015708 | -0.00016457 | -0.00016851 | 2.1032e-05 | -5.539e-06 | -1.1035e-05
1 | 1.3 | All | Covariance | [66 empty] | -1.1013e-06 | -4.3873e-06 | -3.4496e-06 | -2.1583e-07 | -2.7311e-06 | 4.0301e-05
1 | 1.4 | All | Covariance | [66 empty] | -5.5715e-06 | -9.6494e-06 | -2.7575e-06 | 4.3322e-07 | 1.8413e-06 | -6.5615e-07
2 | 2.1 | All | Covariance | [66 empty] | -3.082e-07 | -2.6111e-07 | 1.2739e-07 | -2.1323e-09 | -1.9463e-08 | -1.9495e-09
2 | 2.2 | All | Covariance | [66 empty] | -0.00033662 | -0.00035167 | -0.00052959 | 3.5829e-06 | -9.679e-08 | 4.3398e-07
2 | 2.3 | All | Covariance | [66 empty] | -2.4626e-05 | -2.4229e-05 | -4.1939e-05 | -4.0409e-08 | -1.5852e-05 | 2.6587e-06
2 | 2.4 | All | Covariance | [66 empty] | -5.4115e-05 | -5.152e-05 | -3.0518e-05 | 1.3351e-06 | -1.1454e-05 | 4.8658e-06
Note on D98: Covariance for load V, I measurements only, placed in independent columns
Note on D99: Covariance for load V, I measurements only, placed in independent columns
Note on D100: Covariance for load V, I measurements only, placed in independent columns
Note on D101: Covariance for load V, I measurements only, placed in independent columns
Note on D102: Covariance for load V, I measurements only, placed in independent columns
Note on D103: Covariance for load V, I measurements only, placed in independent columns
Note on D104: Covariance for load V, I measurements only, placed in independent columns
Note on D105: Covariance for load V, I measurements only, placed in independent columns

## Data Scenarios 3-4
Scenario | Data Set | Run | Summary | P_In | P_Secondary | P_Out | P_TransformerLoss | P_ConverterLoss | P_SystemLoss | V_A | V_A_deg | V_AB | V_AB_deg | V_B | V_B_deg | V_BC | V_BC_deg | V_C | V_C_deg | V_CA | V_CA_deg | I_A | I_A_deg | I_B | I_B_deg | I_C | I_C_deg | Delta->Wye P_A | Delta->Wye P_B | Delta->Wye P_C | V_an | V_an_deg | V_bn | V_bn_deg | V_cn | V_cn_deg | I_a | I_an_deg | I_b | I_bn_deg | I_c | I_cn_deg | P_a | P_b | P_c | V_LED_1 | V_LED_2 | V_LED_3 | I_LED_1 | I_LED_2 | I_LED_3 | P_LED_1 | P_LED_2 | P_LED_3 | V_LAPTOP_3_OUTPUT | V_LAPTOP_4_OUTPUT | V_LAPTOP_5_OUTPUT | I_LAPTOP_3_OUTPUT | I_LAPTOP_4_OUTPUT | I_LAPTOP_5_OUTPUT | P_LAPTOP_3_OUTPUT | P_LAPTOP_4_OUTPUT | P_LAPTOP_5_OUTPUT | P_HEATER_1_A | P_HEATER_1_B | P_HEATER_1_C | P_HEATER_2_A | P_HEATER_2_B | P_HEATER_2_C | V_LED_1 * I_LED_1 | V_LED_2 * I_LED_2 | V_LED_3 * I_LED_3 | V_LAPTOP_3_OUTPUT * I_LAPTOP_3_OUTPUT | V_LAPTOP_4_OUTPUT * I_LAPTOP_4_OUTPUT | V_LAPTOP_5_OUTPUT * I_LAPTOP_5_OUTPUT
3 | 3.1 | 3.1.1 | Variance | 0.0014168 | 1.942e-05 | 0.00010441 | 0.0013382 | 0.00015214 | 0.0014842 | 0.0090508 | 1.4817e-29 | 0.022662 | 0 | 0.0067019 | 0 | 0.021696 | 2.1073e-28 | 0.0083653 | 0 | 0.027997 | 0 | 7.8852e-08 | 2.8975e-05 | 1.0938e-07 | 0.00010631 | 5.9764e-08 | 7.9603e-05 | 0.00087831 | 0.00019225 | 3.4865e-05 | 0.0013842 | 5.4428e-35 | 0.0017049 | 0 | 0.0013166 | 2.1073e-28 | 1.7515e-08 | 0.0021139 | 3.4894e-09 | 0.00033682 | 2.6524e-09 | 0.0002447 | 5.0768e-06 | 8.5939e-06 | 7.9065e-07 | 1.0615e-07 | 3.7407e-07 | 1.5118e-07 | 3.1858e-08 | 4.5627e-08 | 4.3146e-08 | 1.88e-05 | 2.6763e-05 | 2.5313e-05 | 2.7904e-09 | 2.3609e-09 | 3.1453e-09 | 9.7253e-09 | 6.5151e-09 | 6.6093e-09 | 3.5054e-06 | 2.2529e-06 | 2.3114e-06 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3.1 | 3.1.2 | Variance | 0.0073419 | 4.7798e-05 | 4.9443e-05 | 0.0074251 | 9.8505e-05 | 0.0071531 | 0.020021 | 1.3171e-29 | 0.076256 | 0 | 0.036129 | 0 | 0.12326 | 7.0243e-29 | 0.033405 | 0 | 0.069178 | 0 | 2.0788e-07 | 2.8628e-05 | 4.5684e-07 | 0.0001873 | 2.4302e-07 | 0.00021642 | 0.0027029 | 0.0015781 | 4.4651e-05 | 0.0047821 | 1.0886e-34 | 0.0043531 | 0 | 0.0077567 | 2.1073e-28 | 1.8812e-08 | 0.0016611 | 5.1834e-07 | 0.021113 | 7.5131e-07 | 0.047514 | 8.8312e-06 | 1.0525e-05 | 1.2641e-05 | 8.6058e-08 | 3.6908e-07 | 5.3353e-07 | 2.9976e-08 | 2.3835e-08 | 2.3715e-08 | 1.7655e-05 | 1.3981e-05 | 1.38e-05 | 1.6925e-09 | 2.4174e-09 | 2.3948e-09 | 6.4606e-09 | 8.302e-09 | 1.8272e-08 | 2.3287e-06 | 2.8707e-06 | 6.3879e-06 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3.1 | 3.1.3 | Variance | 0.0010559 | 2.0676e-05 | 6.2654e-05 | 0.0010912 | 7.2373e-05 | 0.0013322 | 0.0073231 | 1.3171e-29 | 0.019099 | 0 | 0.0052324 | 0 | 0.014401 | 3.5121e-29 | 0.0060799 | 0 | 0.022414 | 0 | 7.982e-08 | 5.6715e-05 | 1.0603e-07 | 0.00011883 | 5.1484e-08 | 0.00011459 | 0.00090367 | 0.00010185 | 6.1228e-05 | 0.0011655 | 1.0048e-34 | 0.0014029 | 0 | 0.00086799 | 2.1073e-28 | 2.1897e-07 | 0.02682 | 9.6842e-09 | 0.0007257 | 5.8872e-09 | 0.00046524 | 2.5052e-06 | 9.8525e-06 | 2.5751e-06 | 1.0272e-07 | 3.4296e-07 | 6.755e-07 | 3.7955e-08 | 5.2142e-08 | 2.3569e-08 | 2.2313e-05 | 3.0592e-05 | 1.378e-05 | 1.3446e-09 | 2.0277e-09 | 3.2087e-09 | 8.8588e-09 | 5.8863e-09 | 2.211e-08 | 3.1931e-06 | 2.0352e-06 | 7.73e-06 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3.2 | 3.2.1 | Variance | 0.082612 | 0.077972 | 0.16394 | 0.00097624 | 0.017601 | 0.015574 | 0.006641 | 2.3597e-29 | 0.017764 | 0 | 0.0062346 | 0 | 0.016665 | 1.4049e-28 | 0.0041812 | 0 | 0.016754 | 0 | 3.362e-07 | 0.0018741 | 3.5254e-07 | 0.0033546 | 1.5898e-07 | 0.0021181 | 0.010218 | 0.0085665 | 0.014574 | 0.001094 | 7.5362e-35 | 0.0010279 | 0 | 0.0010389 | 2.1073e-28 | 5.997e-06 | 0.00076021 | 8.3426e-07 | 0.0012638 | 1.2293e-06 | 0.00075194 | 0.0062755 | 0.0096117 | 0.012118 | 4.555e-06 | 5.7676e-06 | 1.1353e-05 | 3.3222e-05 | 3.1249e-05 | 4.2377e-05 | 0.018781 | 0.017442 | 0.023579 | 1.2281e-06 | 1.1477e-07 | 2.6231e-05 | 7.9994e-08 | 1.6536e-07 | 4.803e-06 | 6.9547e-05 | 5.8464e-05 | 0.0020955 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3.2 | 3.2.2 | Variance | 0.004164 | 0.0025225 | 0.0038725 | 0.0012278 | 0.0051556 | 0.0066877 | 0.0062246 | 1.4817e-29 | 0.019044 | 0 | 0.0065644 | 0 | 0.021893 | 2.1073e-28 | 0.0070764 | 0 | 0.018659 | 0 | 2.6254e-07 | 0.001049 | 7.3322e-08 | 0.0015364 | 8.4014e-08 | 0.00085732 | 0.0039246 | 0.0022943 | 0.0017392 | 0.0012002 | 7.5362e-35 | 0.001184 | 0 | 0.001396 | 3.5121e-29 | 2.5319e-06 | 0.0006823 | 2.9379e-06 | 0.00057208 | 3.5594e-06 | 0.00038426 | 0.0016225 | 0.0018672 | 0.0068543 | 2.2515e-06 | 3.2673e-06 | 8.2599e-06 | 5.0818e-06 | 4.5557e-06 | 3.8321e-06 | 0.002832 | 0.0024335 | 0.0019389 | 5.7618e-07 | 2.4731e-07 | 3.0645e-06 | 3.1079e-07 | 1.3226e-07 | 2.6075e-05 | 0.00015068 | 6.066e-05 | 0.0075739 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3.2 | 3.2.3 | Variance | 0.0043908 | 0.001071 | 0.0062828 | 0.0023246 | 0.0037249 | 0.0045211 | 0.011281 | 1.3171e-29 | 0.034424 | 0 | 0.011758 | 0 | 0.035367 | 5.2682e-29 | 0.01237 | 0 | 0.03646 | 0 | 1.3991e-07 | 0.0016045 | 1.421e-07 | 0.0025109 | 1.27e-07 | 0.0016806 | 0.0022543 | 0.0021268 | 0.0021179 | 0.0022024 | 1.591e-34 | 0.002347 | 0 | 0.0022819 | 1.4049e-28 | 9.9288e-07 | 0.00055053 | 9.7907e-07 | 0.00022895 | 1.2144e-06 | 0.00054963 | 0.001612 | 0.00041284 | 0.00085043 | 1.3384e-06 | 2.091e-06 | 5.9886e-06 | 1.2924e-06 | 1.1112e-06 | 1.5378e-06 | 0.0007732 | 0.0005653 | 0.00074681 | 1.9432e-06 | 1.7641e-07 | 1.0216e-06 | 2.6689e-07 | 1.7845e-07 | 1.8346e-06 | 0.00018655 | 7.3735e-05 | 0.00075037 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3.3 | 3.3.1 | Variance | 0.11975 | 0.10949 | 0.077826 | 0.00098177 | 0.024292 | 0.024997 | 0.011003 | 1.3171e-29 | 0.017894 | 0 | 0.0039218 | 0 | 0.011895 | 2.6341e-29 | 0.007642 | 0 | 0.037933 | 0 | 3.8776e-07 | 0.00035341 | 2.2767e-07 | 0.00075351 | 4.1031e-07 | 0.00071518 | 0.020036 | 0.014222 | 0.02548 | 0.0011394 | 1.4049e-28 | 0.002439 | 6.3639e-34 | 0.00075669 | 0 | 3.4821e-06 | 0.00083915 | 8.7911e-06 | 0.00043884 | 5.4559e-06 | 0.00079447 | 0.01003 | 0.054104 | 0.033407 | 3.8086e-07 | 2.0578e-07 | 6.9385e-07 | 3.3077e-06 | 4.21e-07 | 1.2618e-06 | 0.0018625 | 0.00023238 | 0.0007784 | 5.2586e-07 | 1.0506e-06 | 1.5202e-06 | 2.5205e-06 | 6.1563e-05 | 8.6075e-05 | 0.00075834 | 0.019381 | 0.027464 | 0.0053201 | 0.0081448 | 0.0026229 | 0 | 0 | 0
3 | 3.3 | 3.3.2 | Variance | 0.061862 | 0.065126 | 0.04141 | 0.00092612 | 0.013565 | 0.015027 | 0.0097748 | 1.3171e-29 | 0.024381 | 0 | 0.012442 | 0 | 0.026688 | 2.1073e-28 | 0.0094206 | 0 | 0.043982 | 0 | 3.2034e-07 | 0.001514 | 2.931e-07 | 0.0011064 | 8.6038e-07 | 0.00035205 | 0.0035718 | 0.012264 | 0.030689 | 0.0015939 | 2.1073e-28 | 0.0028394 | 7.0338e-34 | 0.0018547 | 0 | 1.7774e-06 | 0.0025671 | 5.7859e-06 | 0.0010665 | 1.4199e-05 | 0.0017417 | 0.0087945 | 0.0099105 | 0.065793 | 4.7454e-08 | 5.1598e-08 | 1.3161e-07 | 3.7261e-07 | 2.739e-07 | 1.9996e-07 | 0.00021297 | 0.00015473 | 0.0001115 | 5.6773e-07 | 6.4936e-09 | 1.4464e-06 | 2.4697e-07 | 2.1157e-07 | 0.00011849 | 0.00010602 | 6.7761e-05 | 0.037959 | 0.010088 | 0.012104 | 0.014262 | 0 | 0 | 0
3 | 3.3 | 3.3.3 | Variance | 0.050509 | 0.047122 | 0.069869 | 0.0009052 | 0.011309 | 0.011666 | 0.011583 | 1.3171e-29 | 0.020522 | 0 | 0.0094733 | 3.5121e-29 | 0.035913 | 2.1073e-28 | 0.010844 | 0 | 0.039278 | 0 | 1.576e-07 | 0.00057849 | 3.0077e-07 | 0.00056573 | 2.6053e-07 | 0.00048994 | 0.01561 | 0.0216 | 0.014389 | 0.0013133 | 2.1073e-28 | 0.0025593 | 6.6989e-34 | 0.0022883 | 0 | 1.5747e-06 | 0.00053531 | 4.1438e-06 | 8.3526e-05 | 8.3276e-06 | 0.0011674 | 0.033581 | 0.015887 | 0.056825 | 1.9988e-08 | 1.9361e-08 | 1.2995e-07 | 2.3399e-07 | 2.3613e-07 | 1.6618e-07 | 0.00013262 | 0.0001349 | 9.9972e-05 | 1.3782e-07 | 1.6604e-08 | 1.0174e-06 | 2.1019e-07 | 1.0513e-06 | 9.2592e-05 | 6.7235e-05 | 0.00033582 | 0.029733 | 0.043037 | 0.017076 | 0.010134 | 0 | 0 | 0
3 | 3.4 | 3.4.1 | Variance | 0.30616 | 0.26978 | 0.2801 | 0.0037694 | 0.043094 | 0.046081 | 0.015313 | 1.4817e-29 | 0.041427 | 0 | 0.01472 | 0 | 0.048429 | 2.1073e-28 | 0.01708 | 0 | 0.051494 | 0 | 1.4163e-06 | 0.0068275 | 1.2081e-06 | 0.0084294 | 8.5592e-07 | 0.0044663 | 0.16383 | 0.043449 | 0.059274 | 0.0026273 | 2.1073e-28 | 0.0030548 | 1.8757e-33 | 0.0035012 | 0 | 6.9095e-06 | 0.00035686 | 1.3295e-05 | 0.00097016 | 8.9401e-06 | 0.0050176 | 0.047171 | 0.35707 | 0.088224 | 1.5033e-08 | 1.6032e-08 | 1.0811e-08 | 3.5668e-07 | 3.5017e-07 | 1.8464e-07 | 0.00020767 | 0.0002029 | 0.00010779 | 1.332e-05 | 8.1895e-09 | 1.578e-07 | 4.1008e-07 | 3.6984e-06 | 7.671e-06 | 0.00052795 | 0.0012487 | 0.0024325 | 0 | 0 | 0 | 0.041958 | 0.30891 | 0.067215
3 | 3.4 | 3.4.2 | Variance | 0.50757 | 0.43165 | 0.53923 | 0.0041977 | 0.083755 | 0.084486 | 0.015137 | 1.3171e-29 | 0.047876 | 0 | 0.016524 | 0 | 0.047851 | 2.1073e-28 | 0.017404 | 0 | 0.051522 | 0 | 7.952e-07 | 0.00016558 | 3.5688e-07 | 0.0001812 | 6.0507e-07 | 0.00053589 | 0.051757 | 0.095001 | 0.079384 | 0.0030716 | 2.1073e-28 | 0.003503 | 1.0718e-33 | 0.0027738 | 0 | 3.1189e-06 | 0.00022326 | 1.1411e-05 | 0.00035484 | 5.285e-06 | 0.00039504 | 0.058802 | 0.091768 | 0.1865 | 5.247e-09 | 1.0986e-08 | 2.9687e-09 | 1.2684e-06 | 2.2085e-07 | 3.9901e-07 | 0.00073471 | 0.00012782 | 0.00022927 | 1.018e-07 | 8.203e-09 | 2.3718e-08 | 2.0405e-07 | 2.2074e-07 | 1.6186e-06 | 6.1373e-05 | 7.2803e-05 | 0.00051998 | 0 | 0 | 0 | 0.064826 | 0.12189 | 0.17744
3 | 3.4 | 3.4.3 | Variance | 0.35541 | 0.30604 | 0.29084 | 0.0022839 | 0.094355 | 0.10489 | 0.0078771 | 1.3171e-29 | 0.020146 | 0 | 0.0068454 | 0 | 0.028367 | 2.1073e-28 | 0.011203 | 0 | 0.029259 | 0 | 1.0181e-06 | 0.00041484 | 4.9672e-07 | 0.00018073 | 9.3505e-07 | 0.00024636 | 0.088085 | 0.018846 | 0.061285 | 0.0013654 | 3.5121e-29 | 0.0019925 | 2.1436e-33 | 0.002132 | 0 | 4.3542e-06 | 0.00062013 | 1.2432e-05 | 0.00059029 | 2.6748e-06 | 0.00045126 | 0.049729 | 0.1857 | 0.026551 | 1.1051e-08 | 8.6437e-09 | 2.8358e-09 | 7.0168e-07 | 1.3522e-07 | 2.7603e-07 | 0.00040876 | 7.725e-05 | 0.00015964 | 1.6083e-07 | 1.9323e-08 | 1.6693e-07 | 1.9698e-07 | 3.6661e-07 | 1.1025e-05 | 5.6633e-05 | 0.0001261 | 0.0035185 | 0 | 0 | 0 | 0.039985 | 0.18796 | 0.024333
4 | 4.1 | 4.1.1 | Variance | 0.0030071 | 1.7232e-05 | 4.8726e-05 | 0.0031502 | 6.2619e-05 | 0.0032026 | 0.018624 | 1.3171e-29 | 0.04453 | 0 | 0.013906 | 3.5121e-29 | 0.048596 | 2.1073e-28 | 0.019446 | 0 | 0.062796 | 0 | 1.555e-07 | 7.1742e-05 | 2.3704e-07 | 0.00019931 | 1.4223e-07 | 0.00020429 | 0.0017423 | 0.00048117 | 0.00011759 | 0.0028117 | 1.0048e-34 | 0.003975 | 0 | 0.0030742 | 0 | 2.8453e-07 | 0.031723 | 9.4297e-09 | 0.00071187 | 2.4094e-09 | 0.00051048 | 1.0463e-06 | 8.7537e-06 | 3.9913e-06 | 9.4554e-08 | 3.4285e-07 | 6.023e-07 | 1.5492e-08 | 4.4499e-08 | 1.5267e-08 | 9.1391e-06 | 2.6132e-05 | 9.0527e-06 | 1.9142e-09 | 1.4066e-09 | 2.9318e-09 | 5.3899e-09 | 7.0261e-09 | 2.0817e-08 | 1.9429e-06 | 2.4294e-06 | 7.2781e-06 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4.1 | 4.1.2 | Variance | 0.0010189 | 1.482e-05 | 8.4339e-05 | 0.0010217 | 8.6564e-05 | 0.0010817 | 0.0077022 | 1.3171e-29 | 0.016224 | 0 | 0.0038939 | 0 | 0.013049 | 1.4049e-28 | 0.0061581 | 0 | 0.024 | 0 | 1.0051e-07 | 2.6295e-05 | 1.0256e-07 | 0.00017735 | 6.5076e-08 | 5.5475e-05 | 0.00074632 | 0.00012158 | 2.2318e-05 | 0.0010293 | 1.0048e-34 | 0.0015218 | 0 | 0.00083208 | 1.7561e-28 | 9.353e-09 | 0.0010407 | 2.6776e-09 | 0.0003486 | 3.5333e-09 | 0.00028193 | 1.9175e-06 | 8.8055e-06 | 3.3167e-06 | 5.084e-08 | 3.4532e-07 | 5.8986e-07 | 3.4755e-08 | 1.5809e-08 | 1.6966e-08 | 2.0449e-05 | 9.2784e-06 | 9.9567e-06 | 3.0349e-09 | 4.0704e-09 | 3.4749e-09 | 8.2993e-09 | 8.1737e-09 | 2.8916e-08 | 2.9916e-06 | 2.8265e-06 | 1.0111e-05 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4.1 | 4.1.3 | Variance | 0.0015987 | 1.2082e-05 | 7.3735e-05 | 0.0016104 | 9.9254e-05 | 0.0020045 | 0.0064534 | 1.9207e-29 | 0.022286 | 0 | 0.0094875 | 0 | 0.021868 | 1.7561e-28 | 0.0051594 | 0 | 0.019177 | 0 | 1.7377e-07 | 3.8478e-05 | 2.8307e-07 | 0.00020284 | 1.2045e-07 | 0.00039328 | 0.0015406 | 0.00025398 | 0.00020881 | 0.0014092 | 5.8615e-35 | 0.0012174 | 0 | 0.0013911 | 6.1463e-29 | 1.5984e-08 | 0.0019122 | 3.1367e-09 | 0.00030278 | 1.4902e-09 | 0.00036025 | 1.3896e-06 | 9.2281e-06 | 4.3088e-06 | 5.1707e-08 | 3.3909e-07 | 5.6148e-07 | 2.9308e-08 | 4.7639e-08 | 3.5576e-08 | 1.7245e-05 | 2.7932e-05 | 2.0852e-05 | 2.0206e-09 | 3.5514e-09 | 2.0955e-09 | 8.5365e-09 | 8.9945e-09 | 1.1719e-08 | 3.0771e-06 | 3.11e-06 | 4.0978e-06 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4.2 | 4.2.1 | Variance | 0.52204 | 0.46074 | 0.41303 | 0.0035858 | 0.097928 | 0.11928 | 0.011654 | 1.7561e-29 | 0.048103 | 0 | 0.021752 | 0 | 0.058738 | 2.1073e-28 | 0.013951 | 0 | 0.035273 | 0 | 9.8168e-07 | 0.00086386 | 3.5621e-06 | 0.00030386 | 1.5732e-06 | 0.00030433 | 0.023756 | 0.12977 | 0.074456 | 0.003603 | 2.1073e-28 | 0.0022491 | 9.211e-35 | 0.0043663 | 0 | 1.6366e-05 | 0.00019611 | 1.6385e-06 | 0.00056628 | 3.0014e-05 | 0.00063991 | 0.082669 | 0.00017031 | 0.20268 | 8.4234e-09 | 3.6597e-09 | 4.3575e-09 | 5.5549e-07 | 1.527e-07 | 1.0949e-06 | 0.0003212 | 8.8101e-05 | 0.0006285 | 4.8676e-06 | 6.9581e-08 | 2.1488e-06 | 1.5932e-05 | 5.9372e-07 | 0.0001602 | 0.0046785 | 0.0002229 | 0.05151 | 0.029954 | 0 | 0.086186 | 0.029952 | 0 | 0.057995
4 | 4.2 | 4.2.2 | Variance | 0.17414 | 0.1646 | 0.14476 | 0.0012889 | 0.058428 | 0.064558 | 0.0088716 | 1.9207e-29 | 0.029635 | 0 | 0.00989 | 0 | 0.026029 | 2.1073e-28 | 0.0070221 | 0 | 0.021686 | 0 | 2.4995e-07 | 0.0006283 | 1.1205e-06 | 0.00017267 | 1.2737e-06 | 0.00018578 | 0.013656 | 0.039815 | 0.046635 | 0.0019917 | 2.1073e-28 | 0.0013735 | 1.3398e-34 | 0.0017346 | 0 | 3.3577e-06 | 0.00041503 | 1.2141e-06 | 0.00066495 | 1.8211e-05 | 0.00011301 | 0.041974 | 0.00020101 | 0.13812 | 2.0105e-09 | 4.56e-09 | 7.0853e-09 | 1.7262e-07 | 1.8618e-07 | 1.7721e-07 | 0.00010049 | 0.00010765 | 0.00010278 | 7.5647e-07 | 1.0608e-08 | 2.2177e-08 | 1.1778e-05 | 8.3757e-07 | 2.9786e-06 | 0.0036094 | 0.0002671 | 0.00097888 | 0.0055079 | 0 | 0.028316 | 0.020143 | 0 | 0.081516
4 | 4.2 | 4.2.3 | Variance | 0.14011 | 0.14313 | 0.11399 | 0.006308 | 0.07209 | 0.067788 | 0.12119 | 2.1951e-29 | 0.33832 | 0 | 0.11884 | 0 | 0.40124 | 1.0536e-28 | 0.1427 | 0 | 0.40869 | 0 | 3.5382e-06 | 0.0012315 | 1.1666e-05 | 0.0012314 | 5.8074e-06 | 0.00066852 | 0.016637 | 0.038949 | 0.032148 | 0.021988 | 2.6341e-29 | 0.025812 | 8.3736e-35 | 0.025864 | 0 | 5.1143e-05 | 0.00035779 | 2.7644e-06 | 0.0012654 | 9.5736e-05 | 0.00079718 | 0.020221 | 4.9072e-05 | 0.10866 | 4.51e-09 | 7.1531e-09 | 1.3763e-08 | 2.3174e-07 | 1.2632e-07 | 3.1917e-07 | 0.00013429 | 7.2641e-05 | 0.00018402 | 3.0614e-07 | 6.3277e-09 | 3.7616e-08 | 8.516e-07 | 2.2647e-07 | 3.1357e-06 | 0.00024323 | 7.4376e-05 | 0.001014 | 0.0092373 | 0 | 0.037538 | 0.010527 | 0 | 0.053302
4 | 4.3 | 4.3.1 | Variance | 0.96999 | 0.73928 | 0.60928 | 0.028526 | 0.099111 | 0.14411 | 0.018804 | 1.4817e-29 | 0.069795 | 0 | 0.029331 | 0 | 0.085751 | 1.7561e-28 | 0.022953 | 0 | 0.057753 | 0 | 5.7498e-07 | 0.00064649 | 1.3752e-06 | 0.00043231 | 1.6115e-06 | 0.00057539 | 0.03297 | 0.18784 | 0.20916 | 0.004457 | 2.1073e-28 | 0.0040416 | 2.9475e-33 | 0.0051194 | 0 | 1.7396e-06 | 0.0011165 | 8.7139e-06 | 0.00059357 | 2.8362e-05 | 0.0015061 | 0.012927 | 0.079445 | 0.50556 | 4.8003e-09 | 2.3013e-09 | 1.4919e-08 | 2.8221e-07 | 1.9652e-07 | 2.0385e-07 | 0.00016376 | 0.00011301 | 0.00011635 | 2.5055e-06 | 1.4442e-08 | 4.6951e-06 | 9.5396e-06 | 3.5806e-07 | 0.00039215 | 0.0031608 | 0.00012022 | 0.12636 | 0.0064053 | 0 | 0.027657 | 0 | 0.068772 | 0.19515
4 | 4.3 | 4.3.2 | Variance | 0.87728 | 0.74001 | 0.60306 | 0.014242 | 0.10638 | 0.13077 | 0.0093475 | 1.3171e-29 | 0.032663 | 0 | 0.012534 | 0 | 0.03192 | 2.1073e-28 | 0.0095084 | 0 | 0.029612 | 0 | 8.3178e-07 | 0.0010831 | 1.7005e-06 | 0.00073703 | 1.3464e-06 | 0.00028392 | 0.12077 | 0.071543 | 0.17034 | 0.0020854 | 7.0243e-29 | 0.0017338 | 1.4738e-33 | 0.0020045 | 0 | 4.7103e-06 | 0.00070381 | 9.2268e-06 | 0.00086837 | 1.6087e-05 | 0.00029092 | 0.034786 | 0.27409 | 0.12454 | 1.911e-08 | 4.2796e-09 | 2.1085e-09 | 5.5026e-07 | 1.2522e-07 | 1.8778e-07 | 0.00031513 | 7.2176e-05 | 0.00010792 | 1.6516e-06 | 9.0734e-09 | 3.8573e-07 | 2.9868e-05 | 2.7098e-07 | 3.1248e-05 | 0.0091817 | 9.147e-05 | 0.010057 | 0.014569 | 0 | 0.030417 | 0 | 0.19968 | 0.071755
4 | 4.3 | 4.3.3 | Variance | 1.0588 | 1.1981 | 0.82873 | 0.02408 | 0.2701 | 0.30145 | 0.012517 | 1.7561e-29 | 0.05901 | 0 | 0.025211 | 0 | 0.051692 | 2.1073e-28 | 0.010524 | 0 | 0.034148 | 0 | 9.6407e-07 | 0.0006758 | 8.4538e-06 | 0.00089636 | 9.0417e-06 | 0.00086988 | 0.055595 | 0.24744 | 0.39256 | 0.0038369 | 4.3902e-29 | 0.0022857 | 1.0718e-33 | 0.0019997 | 0 | 3.3144e-06 | 0.00058227 | 1.5563e-05 | 0.00064564 | 0.00018916 | 0.0083196 | 0.010231 | 0.21677 | 1.3255 | 4.8238e-09 | 3.8218e-09 | 3.9844e-09 | 2.4098e-07 | 1.0069e-07 | 2.1805e-07 | 0.00013954 | 5.8209e-05 | 0.00012604 | 1.0537e-06 | 1.1261e-08 | 2.8619e-05 | 1.5421e-06 | 6.6679e-07 | 0.0026983 | 0.00053915 | 0.00021347 | 0.87073 | 0.010742 | 0 | 0.016418 | 0 | 0.21459 | 0.13565
4 | 4.4 | 4.4.1 | Variance | 2.7007 | 2.5027 | 2.5439 | 0.0041513 | 0.084497 | 0.09289 | 0.008626 | 1.9207e-29 | 0.018087 | 0 | 0.0058708 | 0 | 0.019968 | 1.0536e-28 | 0.0055563 | 0 | 0.022094 | 0 | 9.0525e-06 | 0.00036254 | 3.5297e-06 | 0.00036275 | 3.3928e-06 | 0.0015004 | 0.46622 | 0.26642 | 0.21744 | 0.001226 | 2.1073e-28 | 0.0015896 | 3.0815e-33 | 0.0012564 | 0 | 5.3625e-05 | 0.00047663 | 5.6508e-05 | 0.00036539 | 7.5727e-07 | 0.00050645 | 0.63364 | 0.62423 | 0.0042039 | 6.8915e-08 | 2.9736e-09 | 6.3948e-08 | 8.6986e-07 | 1.3745e-07 | 1.5459e-07 | 0.00051106 | 7.9175e-05 | 9.0802e-05 | 4.2747e-07 | 1.5983e-08 | 4.6563e-08 | 9.5624e-07 | 2.0614e-07 | 9.0918e-06 | 0.00035147 | 7.0281e-05 | 0.0029823 | 0.0083029 | 0 | 0 | 0.57208 | 0.61626 | 0
4 | 4.4 | 4.4.2 | Variance | 0.82571 | 0.77338 | 0.83849 | 0.0016333 | 0.091473 | 0.095481 | 0.018353 | 1.3171e-29 | 0.038386 | 0 | 0.010221 | 0 | 0.030044 | 1.0536e-28 | 0.014103 | 0 | 0.059641 | 0 | 2.059e-06 | 0.00030535 | 5.8547e-07 | 0.00053677 | 1.8643e-06 | 0.0011843 | 0.18121 | 0.03231 | 0.14247 | 0.0026081 | 1.0536e-28 | 0.003898 | 1.7417e-33 | 0.0019252 | 0 | 6.9978e-06 | 0.00041583 | 1.8531e-05 | 0.0009886 | 4.7524e-06 | 0.0006574 | 0.07434 | 0.33896 | 0.011818 | 3.1796e-07 | 3.2156e-09 | 1.9971e-09 | 3.9754e-07 | 1.7579e-07 | 1.3127e-07 | 0.00024027 | 0.00010151 | 7.537e-05 | 9.2703e-07 | 3.5393e-08 | 2.4165e-07 | 1.9055e-06 | 2.1766e-07 | 2.8002e-05 | 0.0006759 | 6.5457e-05 | 0.0090946 | 0.020532 | 0 | 0 | 0.026155 | 0.40448 | 0
4 | 4.4 | 4.4.3 | Variance | 0.87999 | 0.79786 | 0.57983 | 0.0031138 | 0.10621 | 0.13033 | 0.0077268 | 1.3171e-29 | 0.027201 | 0 | 0.0098902 | 0 | 0.033012 | 2.1073e-28 | 0.009718 | 0 | 0.021774 | 0 | 1.4833e-06 | 0.00027155 | 1.5669e-06 | 0.0026326 | 2.6856e-06 | 0.0043937 | 0.06007 | 0.25527 | 0.21884 | 0.0018413 | 2.1073e-28 | 0.0014353 | 2.6796e-33 | 0.0019301 | 0 | 9.248e-06 | 0.00010602 | 1.3655e-05 | 0.00037262 | 0.00014921 | 0.00029135 | 0.03157 | 0.17053 | 0.79655 | 4.2835e-09 | 4.933e-09 | 7.5294e-09 | 4.3381e-07 | 1.3741e-07 | 1.2001e-07 | 0.00025161 | 7.955e-05 | 6.8761e-05 | 1.5414e-06 | 1.191e-08 | 2.038e-05 | 6.7801e-07 | 4.0443e-07 | 0.0019024 | 0.00013703 | 0.00013352 | 0.61365 | 0.0049094 | 0 | 0 | 0.015107 | 0.15671 | 0
3 | 3.1 | All | Variance | 0.012919 | 1.9856e-05 | 2.083e-05 | 0.012031 | 4.9312e-05 | 0.013587 | 0.046787 | 0 | 0.13189 | 0 | 0.04692 | 0 | 0.14543 | 0.0016242 | 0.04495 | 0 | 0.13877 | 0.00091086 | 1.7414e-07 | 0.00032565 | 4.4822e-07 | 0.00077385 | 2.1194e-07 | 0.0025027 | 0.0042919 | 0.0023035 | 0.00038599 | 0.0082768 | 5.694e-08 | 0.0087618 | 0.00097489 | 0.0091557 | 0.0016937 | 7.7994e-08 | 0.0079794 | 1.5739e-07 | 0.0095488 | 2.2059e-07 | 0.02075 | 1.7017e-05 | 2.0277e-06 | 2.0061e-06 | 3.8043e-07 | 4.2373e-07 | 1.6555e-06 | 3.6068e-09 | 1.6395e-08 | 5.0683e-09 | 2.1145e-06 | 9.5396e-06 | 3.091e-06 | 2.9346e-08 | 8.7816e-08 | 8.4234e-09 | 7.838e-09 | 3.0707e-10 | 1.2681e-08 | 2.8267e-06 | 1.0582e-07 | 4.4381e-06 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3.2 | All | Variance | 1.2021 | 1.1248 | 2.8028 | 0.002396 | 0.37655 | 0.33614 | 0.027853 | 0 | 0.047028 | 0 | 0.012416 | 0 | 0.056449 | 0.00034509 | 0.028899 | 0 | 0.10494 | 7.1182e-05 | 6.5775e-06 | 0.0055829 | 2.909e-06 | 0.0035029 | 8.1975e-07 | 0.0096231 | 0.18731 | 0.028456 | 0.25252 | 0.0026621 | 2.7898e-07 | 0.006204 | 4.8507e-05 | 0.0032287 | 0.00039237 | 9.3008e-05 | 0.017895 | 8.4197e-06 | 0.003705 | 3.6541e-06 | 0.0049301 | 0.044269 | 0.21252 | 0.17328 | 0.00020543 | 0.00028803 | 0.00069005 | 0.00047681 | 0.00064342 | 0.00084962 | 0.26191 | 0.34991 | 0.45411 | 5.4342e-06 | 7.6735e-06 | 7.822e-05 | 1.4242e-06 | 4.344e-07 | 5.748e-05 | 0.00096212 | 3.0602e-06 | 0.012577 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3.3 | All | Variance | 0.031903 | 0.022583 | 0.12544 | 0.0067365 | 0.046892 | 0.068471 | 0.063183 | 0 | 0.13685 | 0 | 0.044695 | 0 | 0.17712 | 0.0011874 | 0.076993 | 0 | 0.24105 | 0.0020526 | 2.3657e-07 | 0.0019669 | 6.8348e-07 | 0.0049985 | 7.8489e-07 | 0.0066418 | 0.0053521 | 0.0031709 | 0.028874 | 0.010339 | 0.0022535 | 0.017573 | 1.2825e-07 | 0.012178 | 3.5191e-06 | 2.5988e-06 | 0.0046775 | 9.073e-06 | 0.017639 | 3.4067e-05 | 0.002274 | 0.012857 | 0.0041472 | 0.1039 | 4.3748e-05 | 4.0507e-05 | 0.00015594 | 6.0488e-05 | 5.2017e-05 | 0.00014632 | 0.032244 | 0.027392 | 0.076342 | 0.00014836 | 8.8642e-06 | 1.9492e-06 | 4.1622e-05 | 1.2268e-07 | 0.00011611 | 0.009349 | 0.00029115 | 0.040943 | 0.042197 | 0.037436 | 0.016548 | 0 | 0 | 0
3 | 3.4 | All | Variance | 7.0754 | 6.919 | 6.228 | 0.0089715 | 0.01819 | 0.033927 | 0.033915 | 0 | 0.044435 | 0 | 0.0074276 | 0 | 0.037905 | 0.00047733 | 0.028689 | 0 | 0.12779 | 0.00014156 | 1.6473e-05 | 0.00016276 | 9.3842e-06 | 0.0038874 | 2.3508e-05 | 0.0080279 | 0.51654 | 0.60093 | 1.4054 | 0.0020097 | 0.00038837 | 0.0069601 | 1.8778e-05 | 0.001772 | 0.0007686 | 4.8248e-05 | 0.010137 | 0.00021319 | 0.00049735 | 7.6336e-05 | 0.0037371 | 0.16444 | 1.7821 | 0.9374 | 6.4263e-07 | 3.5552e-07 | 5.1055e-09 | 9.3974e-09 | 3.4556e-07 | 2.9947e-07 | 9.8368e-06 | 0.00017936 | 0.00017409 | 3.9338e-06 | 2.3925e-07 | 2.0786e-06 | 6.593e-06 | 2.5941e-06 | 0.00019284 | 0.0021397 | 0.00097003 | 0.061967 | 0 | 0 | 0 | 0.12065 | 1.7487 | 0.60018
4 | 4.1 | All | Variance | 0.0013432 | 3.9125e-05 | 1.8456e-07 | 0.0011728 | 4.3914e-05 | 0.0013701 | 0.0062315 | 0 | 0.024734 | 0 | 0.0042263 | 0 | 0.002827 | 0.0010036 | 0.00021576 | 0 | 0.0044391 | 2.7065e-05 | 1.4773e-07 | 0.00025881 | 1.4891e-07 | 0.0019401 | 6.4547e-08 | 3.5586e-05 | 0.0012836 | 8.8121e-05 | 3.6711e-05 | 0.0015727 | 5.6563e-08 | 0.00028155 | 1.3795e-05 | 0.00018574 | 0.00094755 | 2.3847e-07 | 0.02543 | 3.3949e-07 | 0.012677 | 3.2932e-07 | 0.012904 | 3.6301e-08 | 3.497e-06 | 1.9385e-05 | 1.2222e-08 | 4.5297e-08 | 2.0557e-07 | 1.1889e-08 | 3.6981e-08 | 3.0962e-09 | 7.0227e-06 | 2.1669e-05 | 1.8484e-06 | 1.4597e-08 | 5.0509e-08 | 2.1393e-08 | 8.9214e-10 | 5.2742e-10 | 1.7537e-08 | 3.2172e-07 | 1.8229e-07 | 6.1346e-06 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4.2 | All | Variance | 3.7989 | 2.6022 | 2.6623 | 0.15118 | 0.008217 | 0.11064 | 0.1906 | 0 | 0.35786 | 0 | 0.095217 | 0 | 0.39891 | 0.0012601 | 0.20997 | 0 | 0.73152 | 3.7467e-06 | 6.8585e-06 | 0.00050042 | 1.6106e-05 | 0.00020696 | 6.9178e-06 | 0.0021669 | 0.18804 | 0.69724 | 0.51923 | 0.018967 | 2.9858e-06 | 0.046149 | 2.9603e-07 | 0.018594 | 0.00034431 | 6.8421e-05 | 0.0020631 | 1.1014e-05 | 3.6499e-05 | 0.00012816 | 0.0095343 | 0.37448 | 0.00072897 | 1.0109 | 2.425e-07 | 1.7219e-07 | 5.7912e-07 | 7.8568e-07 | 1.3236e-07 | 5.7525e-08 | 0.0004319 | 6.7863e-05 | 2.4372e-05 | 1.1265e-05 | 2.719e-07 | 1.4265e-06 | 3.4985e-06 | 1.9704e-06 | 0.00077531 | 0.0021312 | 0.00069183 | 0.25624 | 0.32874 | 0 | 0.12215 | 0.039518 | 0 | 0.024383
4 | 4.3 | All | Variance | 0.23438 | 0.32432 | 0.50781 | 0.069594 | 0.024999 | 0.10001 | 0.036263 | 0 | 0.13081 | 0 | 0.021112 | 0 | 0.024515 | 7.9137e-05 | 0.0029994 | 0 | 0.025604 | 0.0011438 | 8.3415e-07 | 0.0010842 | 1.8986e-07 | 0.000435 | 3.2024e-07 | 0.0011674 | 0.014996 | 0.034817 | 0.07738 | 0.0083978 | 0.0011226 | 0.00031315 | 2.9459e-07 | 0.0010967 | 0.00085032 | 4.1436e-06 | 0.004049 | 3.1731e-05 | 0.00033135 | 1.7486e-05 | 0.0056321 | 0.013591 | 0.38188 | 0.046306 | 1.6746e-08 | 7.8596e-08 | 2.747e-07 | 1.7201e-06 | 7.8759e-08 | 1.1596e-07 | 0.00098927 | 4.624e-05 | 5.9054e-05 | 4.5208e-06 | 9.1801e-08 | 4.1034e-06 | 3.692e-05 | 3.8374e-07 | 0.00067032 | 0.013535 | 0.00015534 | 0.21993 | 0.0011021 | 0 | 0.054713 | 0 | 0.40043 | 0.11657
4 | 4.4 | All | Variance | 5.1876 | 5.5972 | 5.6608 | 0.029543 | 0.0015454 | 0.044245 | 0.19171 | 0 | 0.87419 | 0 | 0.33813 | 0 | 0.78324 | 0.001954 | 0.16654 | 0 | 0.43213 | 5.3122e-05 | 3.8027e-05 | 0.013658 | 1.9275e-05 | 0.016622 | 1.2045e-05 | 0.019081 | 0.97793 | 0.59955 | 0.27776 | 0.051469 | 9.6208e-05 | 0.027556 | 1.1971e-06 | 0.050198 | 0.0015243 | 0.000449 | 0.0030083 | 6.3603e-05 | 0.0015994 | 5.9491e-05 | 0.0005671 | 2.5637 | 0.20443 | 0.1509 | 4.6881e-06 | 3.1923e-08 | 7.5064e-08 | 1.1223e-07 | 9.9471e-09 | 1.3297e-07 | 0.00011145 | 5.2424e-06 | 7.3642e-05 | 6.28e-06 | 2.5411e-08 | 5.2548e-06 | 2.9893e-06 | 7.3717e-07 | 0.00035985 | 0.00099653 | 0.00022647 | 0.11536 | 0.035717 | 0 | 0 | 2.1711 | 0.20336 | 0
3 | 3.1 | 3.1.1 | Standard Deviation | 0.03764 | 0.0044069 | 0.010218 | 0.036581 | 0.012335 | 0.038525 | 0.095136 | 3.8493e-15 | 0.15054 | 0 | 0.081865 | 0 | 0.14729 | 1.4516e-14 | 0.091462 | 0 | 0.16732 | 0 | 0.00028081 | 0.0053829 | 0.00033073 | 0.010311 | 0.00024447 | 0.008922 | 0.029636 | 0.013865 | 0.0059046 | 0.037205 | 7.3776e-18 | 0.04129 | 0 | 0.036284 | 1.4516e-14 | 0.00013234 | 0.045977 | 5.9071e-05 | 0.018353 | 5.1502e-05 | 0.015643 | 0.0022532 | 0.0029315 | 0.00088919 | 0.0003258 | 0.00061162 | 0.00038882 | 0.00017849 | 0.0002136 | 0.00020772 | 0.0043359 | 0.0051733 | 0.0050312 | 5.2824e-05 | 4.8589e-05 | 5.6083e-05 | 9.8617e-05 | 8.0716e-05 | 8.1298e-05 | 0.0018723 | 0.001501 | 0.0015203 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3.1 | 3.1.2 | Standard Deviation | 0.085685 | 0.0069136 | 0.0070316 | 0.086169 | 0.009925 | 0.084576 | 0.1415 | 3.6291e-15 | 0.27615 | 0 | 0.19008 | 0 | 0.35108 | 8.3811e-15 | 0.18277 | 0 | 0.26302 | 0 | 0.00045594 | 0.0053506 | 0.0006759 | 0.013686 | 0.00049297 | 0.014711 | 0.051989 | 0.039725 | 0.0066821 | 0.069153 | 1.0433e-17 | 0.065978 | 0 | 0.088072 | 1.4516e-14 | 0.00013716 | 0.040757 | 0.00071996 | 0.1453 | 0.00086678 | 0.21798 | 0.0029717 | 0.0032442 | 0.0035554 | 0.00029336 | 0.00060752 | 0.00073043 | 0.00017313 | 0.00015438 | 0.000154 | 0.0042018 | 0.0037391 | 0.0037148 | 4.114e-05 | 4.9167e-05 | 4.8937e-05 | 8.0378e-05 | 9.1115e-05 | 0.00013517 | 0.001526 | 0.0016943 | 0.0025274 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3.1 | 3.1.3 | Standard Deviation | 0.032495 | 0.0045471 | 0.0079154 | 0.033034 | 0.0085072 | 0.036499 | 0.085575 | 3.6291e-15 | 0.1382 | 0 | 0.072336 | 0 | 0.12 | 5.9263e-15 | 0.077974 | 0 | 0.14971 | 0 | 0.00028253 | 0.007531 | 0.00032562 | 0.010901 | 0.0002269 | 0.010705 | 0.030061 | 0.010092 | 0.0078248 | 0.03414 | 1.0024e-17 | 0.037456 | 0 | 0.029462 | 1.4516e-14 | 0.00046795 | 0.16377 | 9.8408e-05 | 0.026939 | 7.6728e-05 | 0.02157 | 0.0015828 | 0.0031389 | 0.0016047 | 0.0003205 | 0.00058563 | 0.00082189 | 0.00019482 | 0.00022835 | 0.00015352 | 0.0047237 | 0.005531 | 0.0037122 | 3.6669e-05 | 4.503e-05 | 5.6645e-05 | 9.4121e-05 | 7.6722e-05 | 0.00014869 | 0.0017869 | 0.0014266 | 0.0027803 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3.2 | 3.2.1 | Standard Deviation | 0.28742 | 0.27923 | 0.40489 | 0.031245 | 0.13267 | 0.12479 | 0.081493 | 4.8577e-15 | 0.13328 | 0 | 0.078959 | 0 | 0.12909 | 1.1853e-14 | 0.064662 | 0 | 0.12944 | 0 | 0.00057983 | 0.043291 | 0.00059375 | 0.057919 | 0.00039872 | 0.046023 | 0.10109 | 0.092556 | 0.12072 | 0.033075 | 8.6812e-18 | 0.03206 | 0 | 0.032231 | 1.4516e-14 | 0.0024489 | 0.027572 | 0.00091338 | 0.03555 | 0.0011088 | 0.027422 | 0.079218 | 0.098039 | 0.11008 | 0.0021342 | 0.0024016 | 0.0033695 | 0.0057638 | 0.0055901 | 0.0065097 | 0.13704 | 0.13207 | 0.15356 | 0.0011082 | 0.00033877 | 0.0051216 | 0.00028283 | 0.00040665 | 0.0021916 | 0.0083395 | 0.0076462 | 0.045776 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3.2 | 3.2.2 | Standard Deviation | 0.064529 | 0.050224 | 0.06223 | 0.03504 | 0.071803 | 0.081778 | 0.078896 | 3.8493e-15 | 0.138 | 0 | 0.081021 | 0 | 0.14796 | 1.4516e-14 | 0.084121 | 0 | 0.1366 | 0 | 0.00051239 | 0.032388 | 0.00027078 | 0.039197 | 0.00028985 | 0.02928 | 0.062647 | 0.047898 | 0.041704 | 0.034644 | 8.6812e-18 | 0.03441 | 0 | 0.037364 | 5.9263e-15 | 0.0015912 | 0.026121 | 0.001714 | 0.023918 | 0.0018866 | 0.019603 | 0.040281 | 0.043211 | 0.082791 | 0.0015005 | 0.0018076 | 0.002874 | 0.0022543 | 0.0021344 | 0.0019576 | 0.053217 | 0.049331 | 0.044033 | 0.00075907 | 0.0004973 | 0.0017506 | 0.00055748 | 0.00036367 | 0.0051064 | 0.012275 | 0.0077885 | 0.087028 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3.2 | 3.2.3 | Standard Deviation | 0.066263 | 0.032727 | 0.079264 | 0.048214 | 0.061032 | 0.067239 | 0.10621 | 3.6291e-15 | 0.18554 | 0 | 0.10844 | 0 | 0.18806 | 7.2582e-15 | 0.11122 | 0 | 0.19094 | 0 | 0.00037404 | 0.040056 | 0.00037696 | 0.050109 | 0.00035637 | 0.040995 | 0.04748 | 0.046118 | 0.046021 | 0.046929 | 1.2613e-17 | 0.048446 | 0 | 0.047769 | 1.1853e-14 | 0.00099644 | 0.023463 | 0.00098948 | 0.015131 | 0.001102 | 0.023444 | 0.040149 | 0.020318 | 0.029162 | 0.0011569 | 0.001446 | 0.0024472 | 0.0011368 | 0.0010541 | 0.0012401 | 0.027806 | 0.023776 | 0.027328 | 0.001394 | 0.00042001 | 0.0010107 | 0.00051661 | 0.00042243 | 0.0013545 | 0.013658 | 0.0085869 | 0.027393 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3.3 | 3.3.1 | Standard Deviation | 0.34605 | 0.33089 | 0.27897 | 0.031333 | 0.15586 | 0.15811 | 0.1049 | 3.6291e-15 | 0.13377 | 0 | 0.062624 | 0 | 0.10907 | 5.1324e-15 | 0.087418 | 0 | 0.19476 | 0 | 0.00062271 | 0.018799 | 0.00047715 | 0.02745 | 0.00064056 | 0.026743 | 0.14155 | 0.11926 | 0.15962 | 0.033755 | 1.1853e-14 | 0.049386 | 2.5227e-17 | 0.027508 | 0 | 0.001866 | 0.028968 | 0.002965 | 0.020948 | 0.0023358 | 0.028186 | 0.10015 | 0.2326 | 0.18278 | 0.00061714 | 0.00045363 | 0.00083298 | 0.0018187 | 0.00064885 | 0.0011233 | 0.043157 | 0.015244 | 0.0279 | 0.00072516 | 0.001025 | 0.0012329 | 0.0015876 | 0.0078462 | 0.0092777 | 0.027538 | 0.13922 | 0.16572 | 0.072939 | 0.090249 | 0.051215 | 0 | 0 | 0
3 | 3.3 | 3.3.2 | Standard Deviation | 0.24872 | 0.2552 | 0.20349 | 0.030432 | 0.11647 | 0.12259 | 0.098867 | 3.6291e-15 | 0.15614 | 0 | 0.11154 | 0 | 0.16336 | 1.4516e-14 | 0.09706 | 0 | 0.20972 | 0 | 0.00056599 | 0.03891 | 0.00054139 | 0.033263 | 0.00092757 | 0.018763 | 0.059764 | 0.11074 | 0.17518 | 0.039924 | 1.4516e-14 | 0.053286 | 2.6521e-17 | 0.043067 | 0 | 0.0013332 | 0.050667 | 0.0024054 | 0.032658 | 0.0037681 | 0.041733 | 0.093779 | 0.099552 | 0.2565 | 0.00021784 | 0.00022715 | 0.00036278 | 0.00061042 | 0.00052336 | 0.00044717 | 0.014593 | 0.012439 | 0.010559 | 0.00075348 | 8.0583e-05 | 0.0012026 | 0.00049696 | 0.00045997 | 0.010885 | 0.010297 | 0.0082317 | 0.19483 | 0.10044 | 0.11002 | 0.11942 | 0 | 0 | 0
3 | 3.3 | 3.3.3 | Standard Deviation | 0.22474 | 0.21708 | 0.26433 | 0.030086 | 0.10634 | 0.10801 | 0.10763 | 3.6291e-15 | 0.14326 | 0 | 0.097331 | 5.9263e-15 | 0.18951 | 1.4516e-14 | 0.10413 | 0 | 0.19819 | 0 | 0.00039699 | 0.024052 | 0.00054843 | 0.023785 | 0.00051042 | 0.022135 | 0.12494 | 0.14697 | 0.11995 | 0.03624 | 1.4516e-14 | 0.050589 | 2.5882e-17 | 0.047836 | 0 | 0.0012549 | 0.023137 | 0.0020356 | 0.0091393 | 0.0028858 | 0.034167 | 0.18325 | 0.12604 | 0.23838 | 0.00014138 | 0.00013914 | 0.00036048 | 0.00048372 | 0.00048593 | 0.00040765 | 0.011516 | 0.011615 | 0.0099986 | 0.00037125 | 0.00012886 | 0.0010087 | 0.00045847 | 0.0010253 | 0.0096225 | 0.0081997 | 0.018325 | 0.17243 | 0.20745 | 0.13068 | 0.10067 | 0 | 0 | 0
3 | 3.4 | 3.4.1 | Standard Deviation | 0.55332 | 0.5194 | 0.52924 | 0.061396 | 0.20759 | 0.21467 | 0.12375 | 3.8493e-15 | 0.20354 | 0 | 0.12133 | 0 | 0.22007 | 1.4516e-14 | 0.13069 | 0 | 0.22692 | 0 | 0.0011901 | 0.082629 | 0.0010991 | 0.091812 | 0.00092516 | 0.066831 | 0.40476 | 0.20844 | 0.24346 | 0.051258 | 1.4516e-14 | 0.05527 | 4.3309e-17 | 0.059171 | 0 | 0.0026286 | 0.018891 | 0.0036462 | 0.031147 | 0.00299 | 0.070835 | 0.21719 | 0.59755 | 0.29703 | 0.00012261 | 0.00012662 | 0.00010398 | 0.00059723 | 0.00059175 | 0.00042969 | 0.014411 | 0.014244 | 0.010382 | 0.0036497 | 9.0496e-05 | 0.00039724 | 0.00064038 | 0.0019231 | 0.0027697 | 0.022977 | 0.035336 | 0.04932 | 0 | 0 | 0 | 0.20484 | 0.5558 | 0.25926
3 | 3.4 | 3.4.2 | Standard Deviation | 0.71244 | 0.657 | 0.73432 | 0.06479 | 0.2894 | 0.29067 | 0.12303 | 3.6291e-15 | 0.2188 | 0 | 0.12855 | 0 | 0.21875 | 1.4516e-14 | 0.13192 | 0 | 0.22698 | 0 | 0.00089174 | 0.012868 | 0.00059739 | 0.013461 | 0.00077786 | 0.023149 | 0.2275 | 0.30822 | 0.28175 | 0.055422 | 1.4516e-14 | 0.059187 | 3.2739e-17 | 0.052667 | 0 | 0.001766 | 0.014942 | 0.003378 | 0.018837 | 0.0022989 | 0.019876 | 0.24249 | 0.30293 | 0.43185 | 7.2436e-05 | 0.00010482 | 5.4486e-05 | 0.0011262 | 0.00046995 | 0.00063167 | 0.027105 | 0.011306 | 0.015142 | 0.00031906 | 9.057e-05 | 0.00015401 | 0.00045171 | 0.00046983 | 0.0012723 | 0.0078341 | 0.0085324 | 0.022803 | 0 | 0 | 0 | 0.25461 | 0.34912 | 0.42123
3 | 3.4 | 3.4.3 | Standard Deviation | 0.59617 | 0.55321 | 0.53929 | 0.04779 | 0.30717 | 0.32387 | 0.088753 | 3.6291e-15 | 0.14194 | 0 | 0.082737 | 0 | 0.16843 | 1.4516e-14 | 0.10585 | 0 | 0.17105 | 0 | 0.001009 | 0.020368 | 0.00070478 | 0.013444 | 0.00096698 | 0.015696 | 0.29679 | 0.13728 | 0.24756 | 0.036952 | 5.9263e-15 | 0.044637 | 4.63e-17 | 0.046174 | 0 | 0.0020867 | 0.024902 | 0.0035259 | 0.024296 | 0.0016355 | 0.021243 | 0.223 | 0.43093 | 0.16295 | 0.00010512 | 9.2971e-05 | 5.3253e-05 | 0.00083766 | 0.00036773 | 0.00052539 | 0.020218 | 0.0087892 | 0.012635 | 0.00040103 | 0.00013901 | 0.00040858 | 0.00044382 | 0.00060549 | 0.0033204 | 0.0075255 | 0.011229 | 0.059317 | 0 | 0 | 0 | 0.19996 | 0.43354 | 0.15599
4 | 4.1 | 4.1.1 | Standard Deviation | 0.054837 | 0.0041512 | 0.0069804 | 0.056127 | 0.0079132 | 0.056591 | 0.13647 | 3.6291e-15 | 0.21102 | 0 | 0.11792 | 5.9263e-15 | 0.22044 | 1.4516e-14 | 0.13945 | 0 | 0.25059 | 0 | 0.00039433 | 0.0084701 | 0.00048687 | 0.014118 | 0.00037713 | 0.014293 | 0.041741 | 0.021936 | 0.010844 | 0.053026 | 1.0024e-17 | 0.063048 | 0 | 0.055446 | 0 | 0.00053341 | 0.17811 | 9.7107e-05 | 0.026681 | 4.9086e-05 | 0.022594 | 0.0010229 | 0.0029587 | 0.0019978 | 0.0003075 | 0.00058553 | 0.00077608 | 0.00012446 | 0.00021095 | 0.00012356 | 0.0030231 | 0.0051119 | 0.0030088 | 4.3751e-05 | 3.7504e-05 | 5.4146e-05 | 7.3416e-05 | 8.3822e-05 | 0.00014428 | 0.0013939 | 0.0015586 | 0.0026978 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4.1 | 4.1.2 | Standard Deviation | 0.03192 | 0.0038497 | 0.0091836 | 0.031964 | 0.009304 | 0.032889 | 0.087762 | 3.6291e-15 | 0.12737 | 0 | 0.062401 | 0 | 0.11423 | 1.1853e-14 | 0.078473 | 0 | 0.15492 | 0 | 0.00031704 | 0.0051278 | 0.00032024 | 0.013317 | 0.0002551 | 0.0074481 | 0.027319 | 0.011026 | 0.0047242 | 0.032083 | 1.0024e-17 | 0.039011 | 0 | 0.028846 | 1.3252e-14 | 9.6711e-05 | 0.032261 | 5.1745e-05 | 0.018671 | 5.9441e-05 | 0.016791 | 0.0013848 | 0.0029674 | 0.0018212 | 0.00022548 | 0.00058764 | 0.00076802 | 0.00018643 | 0.00012573 | 0.00013025 | 0.004522 | 0.003046 | 0.0031554 | 5.509e-05 | 6.38e-05 | 5.8948e-05 | 9.11e-05 | 9.0408e-05 | 0.00017005 | 0.0017296 | 0.0016812 | 0.0031798 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4.1 | 4.1.3 | Standard Deviation | 0.039983 | 0.0034759 | 0.0085869 | 0.040129 | 0.0099627 | 0.044772 | 0.080333 | 4.3826e-15 | 0.14928 | 0 | 0.097404 | 0 | 0.14788 | 1.3252e-14 | 0.071829 | 0 | 0.13848 | 0 | 0.00041686 | 0.0062031 | 0.00053205 | 0.014242 | 0.00034706 | 0.019831 | 0.03925 | 0.015937 | 0.01445 | 0.037539 | 7.6561e-18 | 0.034891 | 0 | 0.037298 | 7.8398e-15 | 0.00012643 | 0.043729 | 5.6007e-05 | 0.017401 | 3.8603e-05 | 0.01898 | 0.0011788 | 0.0030378 | 0.0020758 | 0.00022739 | 0.00058231 | 0.00074932 | 0.0001712 | 0.00021826 | 0.00018862 | 0.0041528 | 0.0052851 | 0.0045665 | 4.4952e-05 | 5.9594e-05 | 4.5776e-05 | 9.2393e-05 | 9.484e-05 | 0.00010826 | 0.0017542 | 0.0017635 | 0.0020243 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4.2 | 4.2.1 | Standard Deviation | 0.72253 | 0.67878 | 0.64267 | 0.059882 | 0.31293 | 0.34537 | 0.10796 | 4.1906e-15 | 0.21932 | 0 | 0.14749 | 0 | 0.24236 | 1.4516e-14 | 0.11812 | 0 | 0.18781 | 0 | 0.0009908 | 0.029392 | 0.0018873 | 0.017432 | 0.0012543 | 0.017445 | 0.15413 | 0.36024 | 0.27287 | 0.060025 | 1.4516e-14 | 0.047425 | 9.5974e-18 | 0.066078 | 0 | 0.0040455 | 0.014004 | 0.00128 | 0.023797 | 0.0054785 | 0.025296 | 0.28752 | 0.01305 | 0.4502 | 9.1779e-05 | 6.0496e-05 | 6.6011e-05 | 0.00074531 | 0.00039077 | 0.0010464 | 0.017922 | 0.0093862 | 0.02507 | 0.0022063 | 0.00026378 | 0.0014659 | 0.0039915 | 0.00077053 | 0.012657 | 0.068399 | 0.01493 | 0.22696 | 0.17307 | 0 | 0.29357 | 0.17307 | 0 | 0.24082
4 | 4.2 | 4.2.2 | Standard Deviation | 0.4173 | 0.40571 | 0.38047 | 0.035902 | 0.24172 | 0.25408 | 0.094189 | 4.3826e-15 | 0.17215 | 0 | 0.099449 | 0 | 0.16133 | 1.4516e-14 | 0.083798 | 0 | 0.14726 | 0 | 0.00049995 | 0.025066 | 0.0010585 | 0.01314 | 0.0011286 | 0.01363 | 0.11686 | 0.19954 | 0.21595 | 0.044628 | 1.4516e-14 | 0.037061 | 1.1575e-17 | 0.041648 | 0 | 0.0018324 | 0.020372 | 0.0011019 | 0.025787 | 0.0042674 | 0.010631 | 0.20488 | 0.014178 | 0.37165 | 4.4838e-05 | 6.7528e-05 | 8.4174e-05 | 0.00041547 | 0.00043149 | 0.00042097 | 0.010025 | 0.010375 | 0.010138 | 0.00086975 | 0.00010299 | 0.00014892 | 0.0034319 | 0.00091519 | 0.0017259 | 0.060078 | 0.016343 | 0.031287 | 0.074215 | 0 | 0.16827 | 0.14193 | 0 | 0.28551
4 | 4.2 | 4.2.3 | Standard Deviation | 0.37431 | 0.37832 | 0.33762 | 0.079423 | 0.2685 | 0.26036 | 0.34813 | 4.6852e-15 | 0.58166 | 0 | 0.34473 | 0 | 0.63344 | 1.0265e-14 | 0.37776 | 0 | 0.63929 | 0 | 0.001881 | 0.035093 | 0.0034155 | 0.035092 | 0.0024099 | 0.025856 | 0.12898 | 0.19735 | 0.1793 | 0.14828 | 5.1324e-15 | 0.16066 | 9.1507e-18 | 0.16082 | 0 | 0.0071514 | 0.018915 | 0.0016626 | 0.035572 | 0.0097845 | 0.028234 | 0.1422 | 0.0070052 | 0.32963 | 6.7156e-05 | 8.4576e-05 | 0.00011731 | 0.0004814 | 0.00035542 | 0.00056495 | 0.011588 | 0.008523 | 0.013565 | 0.0005533 | 7.9547e-05 | 0.00019395 | 0.00092282 | 0.00047588 | 0.0017708 | 0.015596 | 0.0086242 | 0.031843 | 0.096111 | 0 | 0.19375 | 0.1026 | 0 | 0.23087
4 | 4.3 | 4.3.1 | Standard Deviation | 0.98488 | 0.85982 | 0.78056 | 0.1689 | 0.31482 | 0.37961 | 0.13713 | 3.8493e-15 | 0.26419 | 0 | 0.17126 | 0 | 0.29283 | 1.3252e-14 | 0.1515 | 0 | 0.24032 | 0 | 0.00075827 | 0.025426 | 0.0011727 | 0.020792 | 0.0012694 | 0.023987 | 0.18158 | 0.4334 | 0.45734 | 0.066761 | 1.4516e-14 | 0.063573 | 5.4291e-17 | 0.07155 | 0 | 0.0013189 | 0.033413 | 0.0029519 | 0.024363 | 0.0053256 | 0.038809 | 0.1137 | 0.28186 | 0.71103 | 6.9284e-05 | 4.7971e-05 | 0.00012214 | 0.00053123 | 0.00044331 | 0.00045149 | 0.012797 | 0.010631 | 0.010787 | 0.0015829 | 0.00012017 | 0.0021668 | 0.0030886 | 0.00059838 | 0.019803 | 0.056221 | 0.010964 | 0.35547 | 0.080033 | 0 | 0.1663 | 0 | 0.26224 | 0.44176
4 | 4.3 | 4.3.2 | Standard Deviation | 0.93663 | 0.86024 | 0.77657 | 0.11934 | 0.32617 | 0.36162 | 0.096683 | 3.6291e-15 | 0.18073 | 0 | 0.11196 | 0 | 0.17866 | 1.4516e-14 | 0.097511 | 0 | 0.17208 | 0 | 0.00091202 | 0.03291 | 0.001304 | 0.027148 | 0.0011603 | 0.01685 | 0.34751 | 0.26747 | 0.41272 | 0.045666 | 8.3811e-15 | 0.041639 | 3.839e-17 | 0.044771 | 0 | 0.0021703 | 0.026529 | 0.0030376 | 0.029468 | 0.0040109 | 0.017056 | 0.18651 | 0.52354 | 0.3529 | 0.00013824 | 6.5419e-05 | 4.5918e-05 | 0.0007418 | 0.00035387 | 0.00043334 | 0.017752 | 0.0084956 | 0.010389 | 0.0012852 | 9.5255e-05 | 0.00062107 | 0.0054652 | 0.00052055 | 0.00559 | 0.095821 | 0.009564 | 0.10028 | 0.1207 | 0 | 0.1744 | 0 | 0.44685 | 0.26787
4 | 4.3 | 4.3.3 | Standard Deviation | 1.029 | 1.0946 | 0.91035 | 0.15518 | 0.51971 | 0.54904 | 0.11188 | 4.1906e-15 | 0.24292 | 0 | 0.15878 | 0 | 0.22736 | 1.4516e-14 | 0.10258 | 0 | 0.18479 | 0 | 0.00098187 | 0.025996 | 0.0029075 | 0.029939 | 0.0030069 | 0.029494 | 0.23578 | 0.49743 | 0.62655 | 0.061943 | 6.6258e-15 | 0.047809 | 3.2739e-17 | 0.044718 | 0 | 0.0018206 | 0.02413 | 0.003945 | 0.025409 | 0.013753 | 0.091212 | 0.10115 | 0.46559 | 1.1513 | 6.9454e-05 | 6.182e-05 | 6.3122e-05 | 0.0004909 | 0.00031731 | 0.00046696 | 0.011813 | 0.0076295 | 0.011227 | 0.0010265 | 0.00010612 | 0.0053497 | 0.0012418 | 0.00081658 | 0.051946 | 0.02322 | 0.014611 | 0.93313 | 0.10365 | 0 | 0.12813 | 0 | 0.46324 | 0.36831
4 | 4.4 | 4.4.1 | Standard Deviation | 1.6434 | 1.582 | 1.595 | 0.064431 | 0.29068 | 0.30478 | 0.092876 | 4.3826e-15 | 0.13449 | 0 | 0.076621 | 0 | 0.14131 | 1.0265e-14 | 0.074541 | 0 | 0.14864 | 0 | 0.0030087 | 0.01904 | 0.0018788 | 0.019046 | 0.0018419 | 0.038735 | 0.6828 | 0.51616 | 0.46631 | 0.035015 | 1.4516e-14 | 0.03987 | 5.5511e-17 | 0.035445 | 0 | 0.0073229 | 0.021832 | 0.0075172 | 0.019115 | 0.00087021 | 0.022504 | 0.79601 | 0.79008 | 0.064837 | 0.00026252 | 5.4531e-05 | 0.00025288 | 0.00093266 | 0.00037074 | 0.00039317 | 0.022607 | 0.008898 | 0.009529 | 0.00065381 | 0.00012642 | 0.00021578 | 0.00097787 | 0.00045402 | 0.0030153 | 0.018748 | 0.0083834 | 0.054611 | 0.091121 | 0 | 0 | 0.75636 | 0.78502 | 0
4 | 4.4 | 4.4.2 | Standard Deviation | 0.90868 | 0.87942 | 0.91569 | 0.040414 | 0.30244 | 0.309 | 0.13547 | 3.6291e-15 | 0.19592 | 0 | 0.1011 | 0 | 0.17333 | 1.0265e-14 | 0.11876 | 0 | 0.24421 | 0 | 0.0014349 | 0.017474 | 0.00076516 | 0.023168 | 0.0013654 | 0.034413 | 0.42569 | 0.17975 | 0.37745 | 0.051069 | 1.0265e-14 | 0.062434 | 4.1734e-17 | 0.043877 | 0 | 0.0026453 | 0.020392 | 0.0043048 | 0.031442 | 0.00218 | 0.02564 | 0.27265 | 0.58221 | 0.10871 | 0.00056388 | 5.6706e-05 | 4.4689e-05 | 0.00063051 | 0.00041927 | 0.00036231 | 0.015501 | 0.010075 | 0.0086816 | 0.00096282 | 0.00018813 | 0.00049158 | 0.0013804 | 0.00046654 | 0.0052917 | 0.025998 | 0.0080905 | 0.095365 | 0.14329 | 0 | 0 | 0.16172 | 0.63599 | 0
4 | 4.4 | 4.4.3 | Standard Deviation | 0.93808 | 0.89323 | 0.76147 | 0.055801 | 0.3259 | 0.36101 | 0.087902 | 3.6291e-15 | 0.16493 | 0 | 0.09945 | 0 | 0.18169 | 1.4516e-14 | 0.09858 | 0 | 0.14756 | 0 | 0.0012179 | 0.016479 | 0.0012518 | 0.051309 | 0.0016388 | 0.066285 | 0.24509 | 0.50524 | 0.4678 | 0.04291 | 1.4516e-14 | 0.037886 | 5.1764e-17 | 0.043933 | 0 | 0.0030411 | 0.010297 | 0.0036952 | 0.019303 | 0.012215 | 0.017069 | 0.17768 | 0.41295 | 0.8925 | 6.5449e-05 | 7.0235e-05 | 8.6772e-05 | 0.00065864 | 0.00037069 | 0.00034642 | 0.015862 | 0.0089191 | 0.0082922 | 0.0012415 | 0.00010913 | 0.0045145 | 0.00082341 | 0.00063595 | 0.043616 | 0.011706 | 0.011555 | 0.78336 | 0.070067 | 0 | 0 | 0.12291 | 0.39587 | 0
3 | 3.1 | All | Standard Deviation | 0.11366 | 0.004456 | 0.004564 | 0.10969 | 0.0070223 | 0.11656 | 0.2163 | 0 | 0.36316 | 0 | 0.21661 | 0 | 0.38136 | 0.040301 | 0.21201 | 0 | 0.37251 | 0.03018 | 0.0004173 | 0.018046 | 0.00066949 | 0.027818 | 0.00046037 | 0.050027 | 0.065513 | 0.047995 | 0.019647 | 0.090977 | 0.00023862 | 0.093604 | 0.031223 | 0.095685 | 0.041154 | 0.00027927 | 0.089328 | 0.00039672 | 0.097718 | 0.00046967 | 0.14405 | 0.0041251 | 0.001424 | 0.0014164 | 0.00061679 | 0.00065095 | 0.0012867 | 6.0056e-05 | 0.00012804 | 7.1192e-05 | 0.0014541 | 0.0030886 | 0.0017581 | 0.00017131 | 0.00029634 | 9.1779e-05 | 8.8532e-05 | 1.7523e-05 | 0.00011261 | 0.0016813 | 0.00032531 | 0.0021067 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3.2 | All | Standard Deviation | 1.0964 | 1.0606 | 1.6742 | 0.048949 | 0.61364 | 0.57977 | 0.16689 | 0 | 0.21686 | 0 | 0.11143 | 0 | 0.23759 | 0.018577 | 0.17 | 0 | 0.32394 | 0.008437 | 0.0025647 | 0.074719 | 0.0017056 | 0.059185 | 0.0009054 | 0.098097 | 0.43279 | 0.16869 | 0.50252 | 0.051596 | 0.00052819 | 0.078766 | 0.0069647 | 0.056822 | 0.019808 | 0.0096441 | 0.13377 | 0.0029017 | 0.060869 | 0.0019116 | 0.070215 | 0.2104 | 0.461 | 0.41627 | 0.014333 | 0.016972 | 0.026269 | 0.021836 | 0.025366 | 0.029148 | 0.51178 | 0.59153 | 0.67388 | 0.0023311 | 0.0027701 | 0.0088442 | 0.0011934 | 0.00065909 | 0.0075816 | 0.031018 | 0.0017493 | 0.11215 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3.3 | All | Standard Deviation | 0.17861 | 0.15027 | 0.35417 | 0.082076 | 0.21655 | 0.26167 | 0.25136 | 0 | 0.36993 | 0 | 0.21141 | 0 | 0.42085 | 0.034459 | 0.27748 | 0 | 0.49097 | 0.045305 | 0.00048639 | 0.04435 | 0.00082673 | 0.0707 | 0.00088594 | 0.081497 | 0.073158 | 0.056311 | 0.16992 | 0.10168 | 0.047472 | 0.13256 | 0.00035812 | 0.11035 | 0.0018759 | 0.0016121 | 0.068392 | 0.0030121 | 0.13281 | 0.0058367 | 0.047687 | 0.11339 | 0.064399 | 0.32234 | 0.0066143 | 0.0063645 | 0.012487 | 0.0077774 | 0.0072123 | 0.012096 | 0.17957 | 0.1655 | 0.2763 | 0.01218 | 0.0029773 | 0.0013961 | 0.0064515 | 0.00035026 | 0.010776 | 0.09669 | 0.017063 | 0.20234 | 0.20542 | 0.19348 | 0.12864 | 0 | 0 | 0
3 | 3.4 | All | Standard Deviation | 2.66 | 2.6304 | 2.4956 | 0.094718 | 0.13487 | 0.18419 | 0.18416 | 0 | 0.2108 | 0 | 0.086183 | 0 | 0.19469 | 0.021848 | 0.16938 | 0 | 0.35748 | 0.011898 | 0.0040586 | 0.012758 | 0.0030634 | 0.062349 | 0.0048485 | 0.089599 | 0.71871 | 0.7752 | 1.1855 | 0.04483 | 0.019707 | 0.083427 | 0.0043333 | 0.042095 | 0.027724 | 0.0069461 | 0.10068 | 0.014601 | 0.022301 | 0.008737 | 0.061132 | 0.40551 | 1.335 | 0.96819 | 0.00080164 | 0.00059626 | 7.1453e-05 | 9.694e-05 | 0.00058784 | 0.00054724 | 0.0031364 | 0.013393 | 0.013194 | 0.0019834 | 0.00048913 | 0.0014417 | 0.0025677 | 0.0016106 | 0.013887 | 0.046257 | 0.031145 | 0.24893 | 0 | 0 | 0 | 0.34735 | 1.3224 | 0.77471
4 | 4.1 | All | Standard Deviation | 0.036649 | 0.006255 | 0.0004296 | 0.034246 | 0.0066268 | 0.037015 | 0.07894 | 0 | 0.15727 | 0 | 0.06501 | 0 | 0.05317 | 0.03168 | 0.014689 | 0 | 0.066627 | 0.0052024 | 0.00038436 | 0.016088 | 0.00038589 | 0.044046 | 0.00025406 | 0.0059654 | 0.035828 | 0.0093873 | 0.0060589 | 0.039657 | 0.00023783 | 0.016779 | 0.0037142 | 0.013629 | 0.030782 | 0.00048834 | 0.15947 | 0.00058265 | 0.11259 | 0.00057386 | 0.1136 | 0.00019053 | 0.00187 | 0.0044029 | 0.00011055 | 0.00021283 | 0.0004534 | 0.00010904 | 0.0001923 | 5.5644e-05 | 0.00265 | 0.0046549 | 0.0013596 | 0.00012082 | 0.00022474 | 0.00014627 | 2.9869e-05 | 2.2966e-05 | 0.00013243 | 0.0005672 | 0.00042696 | 0.0024768 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4.2 | All | Standard Deviation | 1.9491 | 1.6131 | 1.6317 | 0.38882 | 0.090648 | 0.33262 | 0.43658 | 0 | 0.59821 | 0 | 0.30857 | 0 | 0.63159 | 0.035498 | 0.45822 | 0 | 0.85529 | 0.0019356 | 0.0026189 | 0.02237 | 0.0040133 | 0.014386 | 0.0026302 | 0.04655 | 0.43363 | 0.83501 | 0.72058 | 0.13772 | 0.0017279 | 0.21482 | 0.00054409 | 0.13636 | 0.018556 | 0.0082717 | 0.045421 | 0.0033188 | 0.0060414 | 0.011321 | 0.097644 | 0.61195 | 0.026999 | 1.0055 | 0.00049244 | 0.00041496 | 0.000761 | 0.00088639 | 0.00036382 | 0.00023984 | 0.020782 | 0.0082379 | 0.0049368 | 0.0033563 | 0.00052144 | 0.0011944 | 0.0018704 | 0.0014037 | 0.027844 | 0.046165 | 0.026303 | 0.5062 | 0.57336 | 0 | 0.3495 | 0.19879 | 0 | 0.15615
4 | 4.3 | All | Standard Deviation | 0.48413 | 0.56949 | 0.71261 | 0.26381 | 0.15811 | 0.31624 | 0.19043 | 0 | 0.36168 | 0 | 0.1453 | 0 | 0.15657 | 0.0088959 | 0.054767 | 0 | 0.16001 | 0.03382 | 0.00091332 | 0.032927 | 0.00043572 | 0.020857 | 0.00056589 | 0.034167 | 0.12246 | 0.18659 | 0.27817 | 0.091639 | 0.033505 | 0.017696 | 0.00054276 | 0.033116 | 0.02916 | 0.0020356 | 0.063631 | 0.005633 | 0.018203 | 0.0041816 | 0.075047 | 0.11658 | 0.61796 | 0.21519 | 0.00012941 | 0.00028035 | 0.00052412 | 0.0013115 | 0.00028064 | 0.00034052 | 0.031453 | 0.0068 | 0.0076847 | 0.0021262 | 0.00030299 | 0.0020257 | 0.0060762 | 0.00061947 | 0.025891 | 0.11634 | 0.012463 | 0.46897 | 0.033198 | 0 | 0.23391 | 0 | 0.6328 | 0.34142
4 | 4.4 | All | Standard Deviation | 2.2776 | 2.3659 | 2.3792 | 0.17188 | 0.039312 | 0.21034 | 0.43784 | 0 | 0.93498 | 0 | 0.58149 | 0 | 0.88501 | 0.044204 | 0.40809 | 0 | 0.65737 | 0.0072885 | 0.0061666 | 0.11687 | 0.0043903 | 0.12893 | 0.0034706 | 0.13813 | 0.9889 | 0.7743 | 0.52703 | 0.22687 | 0.0098086 | 0.166 | 0.0010941 | 0.22405 | 0.039042 | 0.02119 | 0.054848 | 0.0079751 | 0.039992 | 0.0077131 | 0.023814 | 1.6012 | 0.45214 | 0.38846 | 0.0021652 | 0.00017867 | 0.00027398 | 0.000335 | 9.9735e-05 | 0.00036465 | 0.010557 | 0.0022896 | 0.0085815 | 0.002506 | 0.00015941 | 0.0022923 | 0.001729 | 0.00085859 | 0.01897 | 0.031568 | 0.015049 | 0.33965 | 0.18899 | 0 | 0 | 1.4735 | 0.45095 | 0
3 | 3.1 | 3.1.1 | Mean | 56.8771 | 5.2978 | 2.8327 | 51.5793 | 2.4651 | 54.0443 | 282.0406 | -30 | 489.1858 | 0 | 282.531 | -150 | 488.8538 | -120.1055 | 281.8487 | 90 | 488.0351 | 119.9635 | 0.3506 | -105.2832 | 0.391 | 130.8461 | 0.35078 | 6.7122 | 24.7306 | 20.6638 | 11.4827 | 123.0277 | 0.061572 | 122.7812 | 120.0348 | 122.9647 | -120.0283 | 0.060033 | -70.4892 | 0.05482 | 42.1744 | 0.047428 | 164.0957 | 2.4592 | 1.4155 | 1.4231 | 24.2671 | 24.2257 | 24.2329 | 0.040798 | 0.021604 | 0.041664 | 0.99005 | 0.52337 | 1.0096 | 18.9852 | 18.5957 | 18.6995 | 0.0027295 | 0.003666 | 0.010144 | 0.051819 | 0.068172 | 0.18968 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3.1 | 3.1.2 | Mean | 56.8004 | 5.2914 | 2.8279 | 51.509 | 2.4635 | 53.9725 | 281.7561 | -30 | 488.8389 | 0 | 282.432 | -150 | 488.7121 | -120.1796 | 281.6828 | 90 | 487.5718 | 119.9218 | 0.35048 | -105.3091 | 0.39125 | 130.7918 | 0.351 | 6.6377 | 24.6823 | 20.6745 | 11.4435 | 122.9406 | 0.061686 | 122.6647 | 119.985 | 122.9292 | -120.105 | 0.060338 | -70.6133 | 0.055333 | 42.0068 | 0.048056 | 163.8385 | 2.4548 | 1.4135 | 1.4231 | 24.2663 | 24.2249 | 24.2316 | 0.040718 | 0.021681 | 0.041523 | 0.98806 | 0.52522 | 1.0062 | 18.9853 | 18.5954 | 18.6993 | 0.0028438 | 0.0036504 | 0.0099795 | 0.053991 | 0.06788 | 0.18661 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3.1 | 3.1.3 | Mean | 56.6534 | 5.2893 | 2.8371 | 51.3642 | 2.4522 | 53.8164 | 281.6161 | -30 | 488.4597 | 0 | 282.1163 | -150 | 488.1339 | -120.1152 | 281.4278 | 90 | 487.2981 | 119.9804 | 0.34983 | -105.3179 | 0.38999 | 130.8295 | 0.35012 | 6.7328 | 24.6009 | 20.5866 | 11.4659 | 122.8458 | 0.062031 | 122.596 | 120.0424 | 122.7841 | -120.0406 | 0.05978 | -70.4399 | 0.055601 | 42.0035 | 0.048347 | 163.8547 | 2.451 | 1.4127 | 1.4256 | 24.2659 | 24.2244 | 24.2303 | 0.040835 | 0.021854 | 0.041579 | 0.9909 | 0.5294 | 1.0075 | 18.9855 | 18.5951 | 18.6993 | 0.0029037 | 0.0036854 | 0.0099279 | 0.055128 | 0.06853 | 0.18564 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3.2 | 3.2.1 | Mean | 414.1025 | 356.4604 | 295.7364 | 57.6421 | 60.7241 | 118.3662 | 283.4057 | -30 | 491.5327 | 0 | 284.1084 | -150 | 491.9892 | -120.0907 | 283.6697 | 90 | 490.798 | 119.9154 | 0.73939 | -63.8729 | 0.73398 | 173.4543 | 0.68309 | 51.6781 | 143.3469 | 144.6589 | 126.0967 | 123.2258 | -0.067432 | 123.0787 | 119.8529 | 123.3277 | -120.1156 | 1.9029 | -58.9114 | 1.8346 | 61.343 | 1.6212 | -174.2285 | 121.3148 | 117.9458 | 117.1999 | 24.1815 | 24.1167 | 24.1606 | 1.1175 | 1.1523 | 1.112 | 27.0232 | 27.7897 | 26.8669 | 18.2823 | 18.1661 | 18.2153 | 3.9762 | 3.9011 | 3.87 | 72.6948 | 70.8683 | 70.4935 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3.2 | 3.2.2 | Mean | 415.5604 | 357.9189 | 298.0501 | 57.6414 | 59.8689 | 117.5103 | 283.5777 | -30 | 491.7127 | 0 | 284.1278 | -150 | 491.9939 | -120.1276 | 283.7402 | 90 | 491.0688 | 119.9058 | 0.74251 | -63.8627 | 0.73594 | 173.397 | 0.68341 | 51.8638 | 144.007 | 144.8387 | 126.7146 | 123.2672 | -0.066616 | 123.1432 | 119.8451 | 123.3255 | -120.1549 | 1.9165 | -59.0594 | 1.8374 | 61.4565 | 1.6227 | -174.157 | 121.6995 | 118.5977 | 117.6217 | 24.1634 | 24.0958 | 24.1294 | 1.1512 | 1.1879 | 1.1523 | 27.816 | 28.6244 | 27.8036 | 18.2809 | 18.1701 | 18.2288 | 3.9752 | 3.9001 | 3.8549 | 72.6709 | 70.8648 | 70.2703 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3.2 | 3.2.3 | Mean | 416.25 | 358.5235 | 298.9893 | 57.7265 | 59.5342 | 117.2607 | 283.7395 | -30 | 491.9644 | 0 | 284.3104 | -150 | 492.4031 | -120.1131 | 283.993 | 90 | 491.4431 | 119.8986 | 0.74448 | -63.9969 | 0.73738 | 173.336 | 0.68479 | 51.8258 | 144.1619 | 144.9961 | 127.0921 | 123.3284 | -0.066443 | 123.2354 | 119.8391 | 123.425 | -120.1394 | 1.9215 | -59.1784 | 1.8404 | 61.4378 | 1.625 | -174.0881 | 121.6547 | 118.8363 | 118.0324 | 24.1532 | 24.0831 | 24.1084 | 1.1584 | 1.2014 | 1.1687 | 27.9802 | 28.9331 | 28.1745 | 18.2777 | 18.1714 | 18.2319 | 3.9739 | 3.8999 | 3.8614 | 72.6333 | 70.867 | 70.4012 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3.3 | 3.3.1 | Mean | 985.1631 | 919.1637 | 852.698 | 65.9993 | 66.4657 | 132.465 | 282.3709 | -30 | 490.0755 | 0 | 283.3911 | -150 | 490.6271 | -120.204 | 282.6901 | 90 | 488.898 | 119.858 | 1.2923 | -43.7704 | 1.3029 | -166.9778 | 1.208 | 73.2001 | 334.9526 | 339.1796 | 311.0309 | 122.0537 | -120.0476 | 121.8689 | -0.17722 | 122.0902 | 119.7851 | 3.1189 | -153.4341 | 2.9674 | -34.3136 | 2.8433 | 90.2322 | 317.8569 | 299.3254 | 301.9814 | 24.1123 | 24.0145 | 24.0453 | 1.1905 | 1.1964 | 1.1549 | 28.706 | 28.7306 | 27.7695 | 18.2123 | 18.2401 | 18.3006 | 3.8813 | 3.8681 | 3.6646 | 70.6867 | 70.555 | 67.0638 | 193.2919 | 180.1808 | 185.7137 | 0 | 0 | 0
3 | 3.3 | 3.3.2 | Mean | 985.5055 | 919.4591 | 853.3187 | 66.0464 | 66.1404 | 132.1868 | 282.3162 | -30 | 490.0807 | 0 | 283.4509 | -150 | 490.7298 | -120.2691 | 282.6918 | 90 | 488.801 | 119.7732 | 1.2915 | -43.8512 | 1.3036 | -167.1105 | 1.209 | 73.0511 | 334.8453 | 339.29 | 311.3702 | 122.0392 | -119.9588 | 121.8307 | -0.17669 | 122.0939 | 119.7883 | 3.116 | -153.3038 | 2.9615 | -34.1538 | 2.8514 | 90.1508 | 317.6678 | 299.1993 | 302.592 | 24.1021 | 24.0045 | 24.0262 | 1.2025 | 1.2077 | 1.1752 | 28.9821 | 28.9903 | 28.2367 | 18.1954 | 18.2447 | 18.303 | 3.8792 | 3.8683 | 3.6831 | 70.5841 | 70.5762 | 67.4121 | 193.1371 | 179.8574 | 185.5427 | 0 | 0 | 0
3 | 3.3 | 3.3.3 | Mean | 985.2461 | 919.3594 | 853.304 | 65.8866 | 66.0554 | 131.942 | 281.9108 | -30 | 489.4374 | 0 | 283.0585 | -150 | 489.955 | -120.217 | 282.2104 | 90 | 488.0033 | 119.8432 | 1.2924 | -43.7792 | 1.3045 | -167.002 | 1.2098 | 73.1829 | 334.8128 | 339.2157 | 311.2175 | 121.8708 | -120.0324 | 121.6226 | -0.17654 | 121.9009 | 119.7849 | 3.1185 | -153.3328 | 2.9634 | -34.05 | 2.8547 | 90.1485 | 317.654 | 299.2395 | 302.4659 | 24.0999 | 24.0027 | 24.0218 | 1.2051 | 1.2098 | 1.1764 | 29.043 | 29.0382 | 28.2587 | 18.1887 | 18.2456 | 18.3031 | 3.8913 | 3.8688 | 3.6833 | 70.7773 | 70.5887 | 67.4163 | 192.8849 | 179.835 | 185.4618 | 0 | 0 | 0
3 | 3.4 | 3.4.1 | Mean | 1616.1921 | 1532.1429 | 1465.0219 | 84.0492 | 67.121 | 151.1702 | 281.6189 | -30 | 489.0994 | 0 | 282.9811 | -150 | 489.8581 | -120.2891 | 282.0582 | 90 | 487.5349 | 119.8122 | 1.9722 | -34.9262 | 1.988 | -156.3243 | 1.9188 | 83.7845 | 539.9007 | 549.0383 | 527.253 | 121.0136 | -120.1921 | 120.6716 | -0.3744 | 120.9665 | 119.5712 | 4.5937 | -143.4498 | 4.5423 | -22.9717 | 4.5284 | 99.762 | 510.7246 | 506.0468 | 515.3716 | 24.0971 | 23.9956 | 24.0169 | 1.2132 | 1.209 | 1.1724 | 29.2338 | 29.0118 | 28.1581 | 18.1908 | 18.2462 | 18.3059 | 3.8848 | 3.8612 | 3.6916 | 70.6672 | 70.4524 | 67.5777 | 0 | 0 | 0 | 385.0871 | 386.3358 | 398.498
3 | 3.4 | 3.4.2 | Mean | 1612.0691 | 1528.1812 | 1461.2575 | 83.8879 | 66.9238 | 150.8116 | 281.6491 | -30 | 489.1096 | 0 | 282.9332 | -150 | 489.7238 | -120.2571 | 282.0046 | 90 | 487.5354 | 119.7955 | 1.9666 | -34.9296 | 1.9843 | -156.3839 | 1.9136 | 83.651 | 538.6358 | 547.8508 | 525.5826 | 121.0078 | -120.1599 | 120.6649 | -0.36793 | 120.9505 | 119.6044 | 4.5829 | -143.3047 | 4.5234 | -22.9282 | 4.523 | 99.647 | 509.9267 | 504.045 | 514.2095 | 24.0962 | 23.9949 | 24.017 | 1.2132 | 1.2098 | 1.1735 | 29.2334 | 29.0298 | 28.1844 | 18.1943 | 18.2467 | 18.3054 | 3.8816 | 3.8637 | 3.694 | 70.623 | 70.5001 | 67.6202 | 0 | 0 | 0 | 384.4191 | 384.3773 | 397.2703
3 | 3.4 | 3.4.3 | Mean | 1611.219 | 1527.1645 | 1460.3014 | 84.0546 | 66.8631 | 150.9177 | 281.9519 | -30 | 489.4695 | 0 | 283.1005 | -150 | 490.1075 | -120.2474 | 282.3211 | 90 | 488.1543 | 119.7892 | 1.9643 | -34.906 | 1.9819 | -156.449 | 1.9091 | 83.6142 | 538.677 | 547.5814 | 524.9607 | 121.0881 | -120.1564 | 120.8126 | -0.36617 | 121.0301 | 119.6262 | 4.5807 | -143.2563 | 4.5136 | -22.9412 | 4.5113 | 99.7405 | 510.1995 | 503.5158 | 513.4492 | 24.0955 | 23.9944 | 24.0171 | 1.213 | 1.2102 | 1.1729 | 29.2282 | 29.0379 | 28.1689 | 18.1943 | 18.2472 | 18.3081 | 3.8867 | 3.8642 | 3.6688 | 70.7155 | 70.5109 | 67.1694 | 0 | 0 | 0 | 384.5878 | 383.8173 | 397.0655
4 | 4.1 | 4.1.1 | Mean | 56.8027 | 5.2822 | 2.8327 | 51.5205 | 2.4494 | 53.97 | 281.9292 | -30 | 489.0954 | 0 | 282.5467 | -150 | 488.8962 | -120.1189 | 281.814 | 90 | 487.8568 | 119.9523 | 0.35102 | -105.3197 | 0.39173 | 130.8118 | 0.35138 | 6.6493 | 24.7177 | 20.6541 | 11.4308 | 123.0055 | 0.061837 | 122.7367 | 120.0118 | 122.9758 | -120.0467 | 0.059707 | -70.4517 | 0.055712 | 41.9222 | 0.048253 | 163.8105 | 2.4497 | 1.4112 | 1.4212 | 24.2654 | 24.224 | 24.2297 | 0.041039 | 0.02165 | 0.041577 | 0.99583 | 0.52444 | 1.0074 | 18.9856 | 18.595 | 18.6992 | 0.0027407 | 0.0036592 | 0.0098923 | 0.052035 | 0.068043 | 0.18498 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4.1 | 4.1.2 | Mean | 56.8261 | 5.2734 | 2.8329 | 51.5527 | 2.4405 | 53.9932 | 281.966 | -30 | 489.1296 | 0 | 282.5306 | -150 | 488.8355 | -120.1787 | 281.796 | 90 | 487.888 | 119.9501 | 0.35178 | -105.3079 | 0.3925 | 130.7284 | 0.35187 | 6.6374 | 24.7665 | 20.6402 | 11.4195 | 123.0133 | 0.062032 | 122.7439 | 120.0139 | 122.9601 | -120.1038 | 0.060359 | -70.6707 | 0.054726 | 42.1187 | 0.047305 | 163.9738 | 2.45 | 1.4086 | 1.4148 | 24.2654 | 24.2238 | 24.2291 | 0.040891 | 0.021594 | 0.04161 | 0.99223 | 0.52309 | 1.0082 | 18.9857 | 18.5948 | 18.6992 | 0.0027006 | 0.0037022 | 0.010123 | 0.051273 | 0.068842 | 0.1893 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4.1 | 4.1.3 | Mean | 56.7543 | 5.27 | 2.8335 | 51.4842 | 2.4365 | 53.9207 | 281.8146 | -30 | 488.8417 | 0 | 282.4269 | -150 | 488.7902 | -120.1308 | 281.7849 | 90 | 487.7602 | 119.9424 | 0.35129 | -105.3398 | 0.39205 | 130.7945 | 0.35175 | 6.6427 | 24.6966 | 20.6363 | 11.4214 | 122.941 | 0.062311 | 122.7119 | 120.0067 | 122.9487 | -120.0552 | 0.060663 | -70.762 | 0.054681 | 42.1158 | 0.047219 | 164.0289 | 2.4497 | 1.4076 | 1.4128 | 24.2652 | 24.2236 | 24.2288 | 0.040826 | 0.021952 | 0.041502 | 0.99066 | 0.53175 | 1.0055 | 18.9859 | 18.5945 | 18.699 | 0.002759 | 0.0036667 | 0.0098955 | 0.052382 | 0.068181 | 0.18504 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4.2 | 4.2.1 | Mean | 1614.4145 | 1520.9663 | 1452.8712 | 93.4482 | 68.0951 | 161.5434 | 282.3256 | -30 | 490.207 | 0 | 283.5152 | -150 | 490.7168 | -120.2421 | 282.6207 | 90 | 488.6923 | 119.8172 | 1.6648 | -21.1974 | 2.6656 | -154.6819 | 1.7929 | 61.1468 | 432.2078 | 745.8448 | 436.362 | 120.3721 | -120.258 | 122.6029 | -0.064137 | 120.2781 | 119.4526 | 6.1278 | -138.2469 | 1.8152 | -57.266 | 6.0348 | 103.775 | 701.5629 | 120.5511 | 698.8523 | 24.095 | 23.9928 | 24.0151 | 1.2139 | 1.2108 | 1.1851 | 29.249 | 29.0503 | 28.4591 | 18.2103 | 18.248 | 18.3205 | 3.8784 | 3.8788 | 3.573 | 70.6273 | 70.7801 | 65.4585 | 192.2081 | 0 | 188.8512 | 383.6492 | 0 | 394.5382
4 | 4.2 | 4.2.2 | Mean | 1617.8604 | 1523.9671 | 1455.8364 | 93.8932 | 68.1307 | 162.024 | 282.262 | -30 | 490.0402 | 0 | 283.4491 | -150 | 490.7107 | -120.2374 | 282.65 | 90 | 488.6916 | 119.8136 | 1.6673 | -21.1639 | 2.6719 | -154.6638 | 1.798 | 61.1469 | 432.8145 | 747.4513 | 437.5945 | 120.3003 | -120.256 | 122.6024 | -0.065225 | 120.2437 | 119.4501 | 6.1396 | -138.1967 | 1.8157 | -57.2724 | 6.0542 | 103.7218 | 702.6789 | 120.5641 | 700.7242 | 24.0945 | 23.9925 | 24.0144 | 1.2152 | 1.2112 | 1.1854 | 29.2798 | 29.0604 | 28.4667 | 18.207 | 18.247 | 18.3181 | 3.8754 | 3.8784 | 3.6199 | 70.5593 | 70.7694 | 66.3093 | 193.0517 | 0 | 189.5422 | 384.0033 | 0 | 394.7943
4 | 4.2 | 4.2.3 | Mean | 1617.7159 | 1523.4929 | 1455.5339 | 94.223 | 67.959 | 162.182 | 283.048 | -30 | 491.1496 | 0 | 284.0135 | -150 | 491.8077 | -120.1784 | 283.4286 | 90 | 490.1734 | 119.8167 | 1.6621 | -21.2063 | 2.6645 | -154.6922 | 1.7943 | 61.0662 | 433.0478 | 747.043 | 437.6251 | 120.5665 | -120.2545 | 122.9747 | -0.064662 | 120.4952 | 119.4834 | 6.1236 | -138.1563 | 1.8097 | -57.2781 | 6.0344 | 103.9111 | 702.5561 | 120.5122 | 700.4245 | 24.094 | 23.992 | 24.0135 | 1.2156 | 1.2115 | 1.1855 | 29.2886 | 29.0666 | 28.4684 | 18.2036 | 18.2473 | 18.319 | 3.875 | 3.8762 | 3.6224 | 70.5392 | 70.7302 | 66.3592 | 193.3026 | 0 | 189.2883 | 383.6697 | 0 | 394.8211
4 | 4.3 | 4.3.1 | Mean | 1613.3789 | 1524.0161 | 1457.6977 | 89.3628 | 66.3184 | 155.6812 | 283.3169 | -30 | 491.6883 | 0 | 284.4154 | -150 | 492.5882 | -120.1849 | 283.8375 | 90 | 490.7239 | 119.8133 | 1.6954 | -44.9708 | 1.9409 | -147.5759 | 2.2613 | 79.7755 | 451.4585 | 537.5456 | 624.3748 | 122.4219 | -119.9762 | 121.4107 | -0.39424 | 120.5408 | 119.5414 | 3.0919 | -152.7917 | 4.5092 | -23.0072 | 6.0248 | 104.2518 | 318.112 | 505.376 | 700.5281 | 24.0928 | 23.9923 | 24.0131 | 1.2161 | 1.213 | 1.1843 | 29.3002 | 29.1034 | 28.4386 | 18.2081 | 18.247 | 18.3346 | 3.8802 | 3.8818 | 3.543 | 70.6507 | 70.8319 | 64.9594 | 193.3185 | 0 | 189.2208 | 0 | 385.4044 | 396.4697
4 | 4.3 | 4.3.2 | Mean | 1612.4215 | 1522.9385 | 1456.3082 | 89.483 | 66.6303 | 156.1133 | 283.4932 | -30 | 491.918 | 0 | 284.3948 | -150 | 492.3626 | -120.1693 | 283.7504 | 90 | 490.8385 | 119.8768 | 1.6937 | -44.979 | 1.9405 | -147.5853 | 2.2608 | 79.7649 | 451.2568 | 537.2825 | 623.8823 | 122.4815 | -120.0412 | 121.4201 | -0.3947 | 120.4758 | 119.5073 | 3.0885 | -152.8603 | 4.4996 | -23.0119 | 6.0324 | 104.1197 | 317.9078 | 504.3235 | 700.7073 | 24.0929 | 23.9923 | 24.014 | 1.2141 | 1.2136 | 1.184 | 29.2523 | 29.1166 | 28.4336 | 18.2082 | 18.247 | 18.3309 | 3.8714 | 3.8816 | 3.593 | 70.4912 | 70.8281 | 65.8622 | 193.3462 | 0 | 188.8131 | 0 | 384.3023 | 395.8626
4 | 4.3 | 4.3.3 | Mean | 1613.0255 | 1523.1577 | 1456.7283 | 89.8678 | 66.4294 | 156.2972 | 283.6974 | -30 | 492.3972 | 0 | 284.6561 | -150 | 492.6634 | -120.1697 | 283.8514 | 90 | 491.04 | 119.8653 | 1.694 | -45.0315 | 1.94 | -147.6158 | 2.2602 | 79.7117 | 451.4779 | 537.6432 | 623.9044 | 122.6018 | -120.0228 | 121.4449 | -0.39533 | 120.5192 | 119.4834 | 3.0882 | -152.9188 | 4.4993 | -23.0408 | 6.0316 | 104.1242 | 317.9125 | 504.2886 | 700.9566 | 24.0926 | 23.9918 | 24.0131 | 1.2166 | 1.2132 | 1.1847 | 29.3115 | 29.1072 | 28.4487 | 18.2044 | 18.2475 | 18.3341 | 3.8685 | 3.8828 | 3.5797 | 70.4242 | 70.8513 | 65.631 | 193.3846 | 0 | 188.8183 | 0 | 384.3145 | 396.4369
4 | 4.4 | 4.4.1 | Mean | 1409.6608 | 1325.182 | 1257.8252 | 84.4789 | 67.3567 | 151.8356 | 283.3394 | -30 | 491.4413 | 0 | 284.1326 | -150 | 492.1407 | -120.1498 | 283.7438 | 90 | 490.8051 | 119.8365 | 2.3125 | -29.2469 | 1.8631 | -178.9561 | 1.1926 | 91.6981 | 642.1684 | 456.1121 | 311.3803 | 120.5964 | -120.3523 | 121.3458 | -0.32496 | 123.3877 | 119.9655 | 6.1403 | -138.2448 | 4.5002 | -22.9411 | 1.5766 | 66.7221 | 704.6835 | 504.0852 | 116.4133 | 24.0938 | 23.9914 | 24.0104 | 1.2167 | 1.214 | 1.1843 | 29.3144 | 29.1246 | 28.4344 | 18.2001 | 18.2474 | 18.3311 | 3.8735 | 3.8816 | 3.6082 | 70.4987 | 70.8299 | 66.1418 | 193.3199 | 0 | 0 | 386.0625 | 384.099 | 0
4 | 4.4 | 4.4.2 | Mean | 1405.6147 | 1321.1256 | 1253.7846 | 84.4891 | 67.341 | 151.8301 | 283.3342 | -30 | 491.7721 | 0 | 284.4238 | -150 | 492.4799 | -120.187 | 283.7437 | 90 | 490.6303 | 119.8222 | 2.3062 | -29.3551 | 1.8566 | -179.0371 | 1.1893 | 91.6902 | 640.4402 | 454.6536 | 310.5209 | 120.6696 | -120.3331 | 121.298 | -0.3243 | 123.4808 | 119.9413 | 6.1149 | -138.2784 | 4.497 | -22.9486 | 1.5629 | 66.7519 | 701.9884 | 503.5007 | 115.6365 | 24.0955 | 23.9913 | 24.0101 | 1.2171 | 1.2141 | 1.185 | 29.3278 | 29.129 | 28.4515 | 18.2019 | 18.2477 | 18.3356 | 3.8702 | 3.8802 | 3.5702 | 70.4444 | 70.8042 | 65.4625 | 193.0485 | 0 | 0 | 383.5649 | 383.5518 | 0
4 | 4.4 | 4.4.3 | Mean | 1405.8255 | 1321.044 | 1253.6284 | 84.7815 | 67.4156 | 152.1971 | 284.0952 | -30 | 493.2006 | 0 | 285.2532 | -150 | 493.8148 | -120.2379 | 284.4506 | 90 | 491.8462 | 119.8317 | 2.3001 | -29.4804 | 1.8548 | -179.2086 | 1.1857 | 91.455 | 640.4714 | 454.932 | 310.4221 | 121.0208 | -120.3389 | 121.6064 | -0.32282 | 123.8139 | 119.8891 | 6.0982 | -138.352 | 4.485 | -23.0138 | 1.5636 | 66.7049 | 701.8381 | 503.1954 | 116.0105 | 24.0981 | 23.991 | 24.0099 | 1.2173 | 1.2141 | 1.1846 | 29.3353 | 29.1277 | 28.4427 | 18.205 | 18.2477 | 18.334 | 3.8725 | 3.8801 | 3.5889 | 70.4994 | 70.8035 | 65.7997 | 192.9563 | 0 | 0 | 383.4591 | 383.2046 | 0
3 | 3.1 | All | Mean | 56.777 | 5.2928 | 2.8326 | 51.4841 | 2.4603 | 53.9444 | 281.8043 | -30 | 488.8281 | 0 | 282.3597 | -150 | 488.5666 | -120.1334 | 281.6531 | 90 | 487.635 | 119.9552 | 0.3503 | -105.3034 | 0.39075 | 130.8225 | 0.35063 | 6.6942 | 24.6713 | 20.6416 | 11.4641 | 122.938 | 0.061763 | 122.6806 | 120.0207 | 122.8926 | -120.058 | 0.06005 | -70.5141 | 0.055251 | 42.0616 | 0.047944 | 163.9297 | 2.455 | 1.4139 | 1.4239 | 24.2664 | 24.225 | 24.2316 | 0.040784 | 0.021713 | 0.041589 | 0.98967 | 0.526 | 1.0078 | 18.9853 | 18.5954 | 18.6993 | 0.0028257 | 0.0036672 | 0.010017 | 0.053646 | 0.068194 | 0.18731 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3.2 | All | Mean | 415.3043 | 357.6343 | 297.5919 | 57.67 | 60.0424 | 117.7124 | 283.5743 | -30 | 491.7366 | 0 | 284.1822 | -150 | 492.1287 | -120.1105 | 283.801 | 90 | 491.1033 | 119.9066 | 0.74213 | -63.9108 | 0.73576 | 173.3958 | 0.68376 | 51.7892 | 143.8386 | 144.8312 | 126.6345 | 123.2738 | -0.066831 | 123.1524 | 119.8457 | 123.3594 | -120.1366 | 1.9136 | -59.0497 | 1.8375 | 61.4124 | 1.6229 | -174.1578 | 121.5563 | 118.4599 | 117.618 | 24.166 | 24.0985 | 24.1328 | 1.1424 | 1.1805 | 1.1443 | 27.6065 | 28.4491 | 27.615 | 18.2803 | 18.1692 | 18.2254 | 3.9751 | 3.9004 | 3.8621 | 72.6664 | 70.8667 | 70.3883 | 0 | 0 | 0 | 0 | 0 | 0
3 | 3.3 | All | Mean | 985.3049 | 919.3274 | 853.1069 | 65.9774 | 66.2205 | 132.1979 | 282.1993 | -30 | 489.8645 | 0 | 283.3001 | -150 | 490.4373 | -120.23 | 282.5308 | 90 | 488.5674 | 119.8248 | 1.2921 | -43.8003 | 1.3037 | -167.0301 | 1.209 | 73.1447 | 334.8702 | 339.2284 | 311.2062 | 121.9879 | -120.013 | 121.7741 | -0.17681 | 122.0283 | 119.7861 | 3.1178 | -153.3569 | 2.9641 | -34.1725 | 2.8498 | 90.1772 | 317.7262 | 299.2547 | 302.3464 | 24.1048 | 24.0072 | 24.0311 | 1.1994 | 1.2046 | 1.1688 | 28.9104 | 28.9197 | 28.0883 | 18.1988 | 18.2435 | 18.3022 | 3.8839 | 3.8684 | 3.677 | 70.6827 | 70.5733 | 67.2974 | 193.1047 | 179.9577 | 185.5727 | 0 | 0 | 0
3 | 3.4 | All | Mean | 1613.1601 | 1529.1629 | 1462.1936 | 83.9972 | 66.9693 | 150.9665 | 281.74 | -30 | 489.2262 | 0 | 283.0049 | -150 | 489.8965 | -120.2645 | 282.128 | 90 | 487.7415 | 119.799 | 1.9677 | -34.9206 | 1.9847 | -156.3857 | 1.9138 | 83.6832 | 539.0712 | 548.1568 | 525.9321 | 121.0365 | -120.1694 | 120.7164 | -0.3695 | 120.9824 | 119.6006 | 4.5858 | -143.3369 | 4.5264 | -22.947 | 4.5209 | 99.7165 | 510.2836 | 504.5359 | 514.3434 | 24.0962 | 23.995 | 24.017 | 1.2131 | 1.2097 | 1.1729 | 29.2318 | 29.0265 | 28.1705 | 18.1931 | 18.2467 | 18.3065 | 3.8844 | 3.863 | 3.6848 | 70.6685 | 70.4878 | 67.4558 | 0 | 0 | 0 | 384.698 | 384.8435 | 397.6113
4 | 4.1 | All | Mean | 56.7944 | 5.2752 | 2.8331 | 51.5192 | 2.4421 | 53.9613 | 281.9033 | -30 | 489.0222 | 0 | 282.5014 | -150 | 488.8407 | -120.1428 | 281.7983 | 90 | 487.835 | 119.9483 | 0.35136 | -105.3225 | 0.3921 | 130.7782 | 0.35166 | 6.6432 | 24.7269 | 20.6435 | 11.4239 | 122.9866 | 0.06206 | 122.7308 | 120.0108 | 122.9615 | -120.0686 | 0.060243 | -70.6281 | 0.055039 | 42.0522 | 0.047593 | 163.9378 | 2.4498 | 1.4091 | 1.4163 | 24.2653 | 24.2238 | 24.2292 | 0.040919 | 0.021732 | 0.041563 | 0.99291 | 0.52643 | 1.007 | 18.9857 | 18.5948 | 18.6991 | 0.0027335 | 0.003676 | 0.0099704 | 0.051897 | 0.068355 | 0.18644 | 0 | 0 | 0 | 0 | 0 | 0
4 | 4.2 | All | Mean | 1616.6636 | 1522.8088 | 1454.7472 | 93.8548 | 68.0616 | 161.9164 | 282.5452 | -30 | 490.4656 | 0 | 283.6593 | -150 | 491.0784 | -120.2193 | 282.8998 | 90 | 489.1858 | 119.8159 | 1.6647 | -21.1892 | 2.6673 | -154.6793 | 1.795 | 61.12 | 432.69 | 746.7797 | 437.1939 | 120.413 | -120.2562 | 122.7267 | -0.064675 | 120.339 | 119.462 | 6.1303 | -138.2 | 1.8135 | -57.2722 | 6.0411 | 103.8026 | 702.266 | 120.5425 | 700.0003 | 24.0945 | 23.9924 | 24.0143 | 1.2149 | 1.2112 | 1.1853 | 29.2725 | 29.0591 | 28.4648 | 18.2069 | 18.2474 | 18.3192 | 3.8763 | 3.8778 | 3.6051 | 70.5752 | 70.7599 | 66.0423 | 192.8542 | 0 | 189.2272 | 383.7741 | 0 | 394.7179
4 | 4.3 | All | Mean | 1612.942 | 1523.3708 | 1456.9114 | 89.5712 | 66.4594 | 156.0306 | 283.5025 | -30 | 492.0012 | 0 | 284.4888 | -150 | 492.5381 | -120.1747 | 283.8131 | 90 | 490.8675 | 119.8518 | 1.6944 | -44.9938 | 1.9404 | -147.5923 | 2.2608 | 79.7507 | 451.3977 | 537.4904 | 624.0538 | 122.5017 | -120.0134 | 121.4252 | -0.39476 | 120.5119 | 119.5107 | 3.0896 | -152.857 | 4.5027 | -23.02 | 6.0296 | 104.1652 | 317.9774 | 504.6627 | 700.7306 | 24.0928 | 23.9922 | 24.0134 | 1.2156 | 1.2133 | 1.1844 | 29.288 | 29.1091 | 28.4403 | 18.2069 | 18.2472 | 18.3332 | 3.8734 | 3.8821 | 3.5719 | 70.522 | 70.8371 | 65.4842 | 193.3498 | 0 | 188.9508 | 0 | 384.6737 | 396.2564
4 | 4.4 | All | Mean | 1407.0337 | 1322.4505 | 1255.0794 | 84.5832 | 67.3711 | 151.9543 | 283.5896 | -30 | 492.138 | 0 | 284.6032 | -150 | 492.8118 | -120.1916 | 283.9794 | 90 | 491.0939 | 119.8302 | 2.3063 | -29.3608 | 1.8582 | -179.0673 | 1.1892 | 91.6145 | 641.0267 | 455.2326 | 310.7744 | 120.7623 | -120.3414 | 121.4168 | -0.32403 | 123.5608 | 119.932 | 6.1178 | -138.2917 | 4.4941 | -22.9678 | 1.5677 | 66.7263 | 702.8367 | 503.5938 | 116.0201 | 24.0958 | 23.9912 | 24.0101 | 1.2171 | 1.2141 | 1.1846 | 29.3258 | 29.1271 | 28.4429 | 18.2023 | 18.2476 | 18.3336 | 3.8721 | 3.8806 | 3.5891 | 70.4809 | 70.8126 | 65.8013 | 193.1082 | 0 | 0 | 384.3622 | 383.6185 | 0
3 | 3.1 | All | Covariance | [66 empty] | -5.1321e-09 | -7.7998e-08 | 5.5532e-08 | 1.4769e-08 | -2.6094e-09 | 1.024e-08
3 | 3.2 | All | Covariance | [66 empty] | -0.0003071 | -0.00042769 | -0.00075964 | 2.7548e-06 | -1.8138e-06 | -5.4538e-05
3 | 3.3 | All | Covariance | [66 empty] | -5.144e-05 | -4.5903e-05 | -0.00014978 | -4.7149e-05 | 8.3271e-07 | 1.5039e-05
3 | 3.4 | All | Covariance | [66 empty] | 5.8754e-08 | -3.4649e-07 | 2.3906e-08 | -7.2257e-07 | 7.2919e-07 | -1.9972e-05
4 | 4.1 | All | Covariance | [66 empty] | 1.1196e-08 | -2.9585e-08 | 1.5085e-08 | 1.3054e-09 | -5.2455e-10 | 6.5241e-09
4 | 4.2 | All | Covariance | [66 empty] | -4.1988e-07 | -1.4769e-07 | -1.6892e-07 | 5.6835e-06 | 2.237e-07 | -3.0262e-05
4 | 4.3 | All | Covariance | [66 empty] | -1.573e-07 | 1.354e-08 | -1.441e-07 | 8.7101e-06 | 1.8481e-07 | -4.1262e-05
4 | 4.4 | All | Covariance | [66 empty] | 6.7091e-07 | -9.0991e-09 | -5.4866e-08 | -6.2413e-07 | -1.3681e-07 | -4.2978e-05
Note on D98: Covariance for load V, I measurements only, placed in independent columns
Note on D99: Covariance for load V, I measurements only, placed in independent columns
Note on D100: Covariance for load V, I measurements only, placed in independent columns
Note on D101: Covariance for load V, I measurements only, placed in independent columns
Note on D102: Covariance for load V, I measurements only, placed in independent columns
Note on D103: Covariance for load V, I measurements only, placed in independent columns
Note on D104: Covariance for load V, I measurements only, placed in independent columns
Note on D105: Covariance for load V, I measurements only, placed in independent columns

## Data Scenarios 5-6
Scenario | Data Set | Run | Summary | P_In | P_Secondary | P_Out | P_TransformerLoss | P_ConverterLoss | P_SystemLoss | V_A | V_A_deg | V_AB | V_AB_deg | V_B | V_B_deg | V_BC | V_BC_deg | V_C | V_C_deg | V_CA | V_CA_deg | I_A | I_A_deg | I_B | I_B_deg | I_C | I_C_deg | Delta->Wye P_A | Delta->Wye P_B | Delta->Wye P_C | V_Nextek_Input | V_Nextek_Input_deg | I_Nextek_Input | I_Nextek_Input_deg | P_Nextek_Input | V_LED_1 | V_LED_2 | V_LED_3 | I_LED_1 | I_LED_2 | I_LED_3 | P_LED_1 | P_LED_2 | P_LED_3 | V_LAPTOP_4_INPUT | V_LAPTOP_4_OUTPUT | V_LAPTOP_5_INPUT | V_LAPTOP_5_OUTPUT | V_LAPTOP_6_INPUT | V_LAPTOP_6_OUTPUT | I_LAPTOP_4_INPUT | I_LAPTOP_4_OUTPUT | I_LAPTOP_5_INPUT | I_LAPTOP_5_OUTPUT | I_LAPTOP_6_INPUT | I_LAPTOP_6_OUTPUT | P_LAPTOP_4_INPUT | P_LAPTOP_4_OUTPUT | P_LAPTOP_5_INPUT | P_LAPTOP_5_OUTPUT | P_LAPTOP_6_INPUT | P_LAPTOP_6_OUTPUT | V_RESISTOR_1A | V_RESISTOR_1B | V_RESISTOR_1C | V_RESISTOR_1D | V_RESISTOR_1E | V_RESISTOR_1F | V_RESISTOR_1G | P_RESISTOR_1A | P_RESISTOR_1B | P_RESISTOR_1C | P_RESISTOR_1D | P_RESISTOR_1E | P_RESISTOR_1F | P_RESISTOR_1G | V_LED_1 * I_LED_1 | V_LED_2 * I_LED_2 | V_LED_3 * I_LED_3 | V_LAPTOP_4_OUTPUT * I_LAPTOP_4_OUTPUT | V_LAPTOP_5_OUTPUT * I_LAPTOP_5_OUTPUT | V_LAPTOP_6_OUTPUT * I_LAPTOP_6_OUTPUT
5 | 5.1 | 5.1.1 | Variance | 0.0019181 | 0.0002821 | 5.2995e-06 | 0.0018985 | 0.00031247 | 0.001853 | 0.0077403 | 1.6463e-29 | 0.036945 | 0 | 0.014694 | 0 | 0.032479 | 7.9023e-29 | 0.0068717 | 0 | 0.018535 | 0 | 1.3308e-07 | 0.00011125 | 2.1549e-07 | 0.00084188 | 9.2424e-08 | 0.00041905 | 0.001059 | 0.00072599 | 0.00024258 | 0.0023409 | 4.8148e-35 | 5.0503e-08 | 0.00048117 | 0.0002821 | 9.1525e-09 | 4.1995e-09 | 5.0417e-09 | 0 | 0 | 0 | 4.1141e-13 | 2.1868e-13 | 3.1768e-13 | 8.1171e-09 | 7.2759e-07 | 7.7617e-09 | 8.3456e-07 | 8.917e-09 | 7.478e-07 | 9.7918e-08 | 7.1925e-09 | 3.847e-08 | 5.9182e-09 | 8.8853e-08 | 1.768e-08 | 5.9065e-05 | 2.5752e-06 | 2.3167e-05 | 2.0865e-06 | 5.3615e-05 | 6.2427e-06 | 5.6501e-14 | 4.037e-14 | 4.4572e-14 | 4.999e-14 | 3.6803e-14 | 3.4094e-14 | 2.5865e-14 | 1.1328e-62 | 3.8076e-63 | 1.6872e-63 | 9.8553e-64 | 8.0365e-63 | 1.0016e-63 | 4.7666e-64
5 | 5.1 | 5.1.2 | Variance | 0.0012421 | 0.00011793 | 6.7897e-06 | 0.0010609 | 0.00011872 | 0.0012508 | 0.0081039 | 1.7561e-29 | 0.019578 | 0 | 0.0061395 | 0 | 0.019936 | 8.7804e-29 | 0.0066254 | 0 | 0.023117 | 0 | 8.0387e-08 | 0.0001011 | 7.3792e-08 | 0.00056489 | 5.0711e-08 | 7.2146e-05 | 0.0006291 | 0.00056288 | 3.4696e-05 | 0.0012394 | 3.9775e-35 | 4.3308e-08 | 0.00016696 | 0.00011793 | 6.9649e-09 | 2.8161e-09 | 4.8148e-09 | 0 | 0 | 0 | 1.8384e-13 | 2.0924e-13 | 4.2624e-13 | 3.9342e-09 | 1.9106e-07 | 3.3114e-09 | 4.5316e-07 | 3.6569e-09 | 2.3527e-07 | 7.4833e-08 | 7.0227e-09 | 5.6087e-08 | 8.5582e-09 | 2.5537e-08 | 9.2929e-09 | 4.5123e-05 | 2.4966e-06 | 3.381e-05 | 3.0192e-06 | 1.54e-05 | 3.292e-06 | 3.8011e-14 | 5.2875e-14 | 6.3435e-14 | 9.3615e-14 | 7.52e-14 | 6.6663e-14 | 3.3402e-14 | 5.1076e-63 | 3.8766e-63 | 1.372e-63 | 1.519e-63 | 1.4403e-62 | 5.1372e-64 | 2.2633e-64
5 | 5.1 | 5.1.3 | Variance | 0.0019422 | 0.00026008 | 1.2026e-05 | 0.0020065 | 0.00024136 | 0.0019216 | 0.0078964 | 1.3171e-29 | 0.034309 | 0 | 0.013269 | 0 | 0.030342 | 2.1073e-28 | 0.0069743 | 0 | 0.019764 | 0 | 7.4694e-08 | 0.00013514 | 1.117e-07 | 0.0004444 | 5.7971e-08 | 0.00021068 | 0.00062564 | 0.00082456 | 8.0141e-05 | 0.0021722 | 3.3494e-35 | 2.8564e-08 | 0.00036504 | 0.00026008 | 9.867e-09 | 4.9885e-09 | 6.8082e-09 | 0 | 0 | 0 | 3.9011e-13 | 1.4828e-13 | 6.0004e-13 | 4.3816e-09 | 1.372e-07 | 2.9395e-09 | 1.7911e-07 | 2.7299e-09 | 1.8226e-07 | 2.7151e-08 | 1.0628e-08 | 7.0727e-08 | 4.4279e-09 | 4.7358e-08 | 1.562e-08 | 1.6369e-05 | 3.7822e-06 | 4.2643e-05 | 1.5596e-06 | 2.8553e-05 | 5.5373e-06 | 4.3207e-14 | 4.7618e-14 | 4.6071e-14 | 5.4071e-14 | 6.9897e-14 | 4.7246e-14 | 3.4496e-14 | 7.2581e-63 | 4.2138e-63 | 1.876e-63 | 1.5602e-63 | 1.6099e-62 | 8.3965e-64 | 1.8009e-64
5 | 5.2 | 5.2.1 | Variance | 0.063734 | 0.067541 | 0.096117 | 0.0010989 | 0.0043043 | 0.0048684 | 0.005899 | 1.3171e-29 | 0.012209 | 0 | 0.0059624 | 0 | 0.01819 | 2.1073e-28 | 0.0067652 | 0 | 0.025646 | 0 | 5.3956e-07 | 0.0081964 | 3.8299e-07 | 0.00054128 | 7.6093e-08 | 0.00019931 | 0.019555 | 0.014226 | 0.00012027 | 0.00079585 | 9.0435e-34 | 8.3031e-06 | 0.0042099 | 0.067541 | 1.2337e-07 | 4.0754e-07 | 1.1192e-07 | 1.9842e-05 | 9.1647e-06 | 9.5069e-06 | 0.011722 | 0.0052928 | 0.0055757 | 7.9087e-09 | 3.5622e-05 | 6.8127e-09 | 1.5939e-06 | 5.4563e-08 | 2.9526e-06 | 2.1055e-07 | 1.1796e-07 | 1.1242e-07 | 2.4292e-07 | 1.1545e-05 | 1.511e-05 | 0.00012613 | 4.5956e-05 | 6.7438e-05 | 9.0565e-05 | 0.0068918 | 0.0052383 | 1.0605e-08 | 5.2785e-11 | 7.2783e-12 | 5.2422e-12 | 0.012974 | 5.4846e-12 | 1.4209e-11 | 5.2612e-07 | 2.3998e-56 | 1.9004e-58 | 2.5917e-59 | 1.4912e-41 | 1.3262e-58 | 8.6705e-57
5 | 5.2 | 5.2.2 | Variance | 0.02183 | 0.017719 | 0.010876 | 0.0018577 | 0.0019864 | 0.0056414 | 0.013343 | 1.7561e-29 | 0.036596 | 0 | 0.0082298 | 0 | 0.02018 | 7.0243e-29 | 0.0088947 | 0 | 0.034612 | 0 | 6.5911e-08 | 0.0032006 | 9.7044e-08 | 0.00071997 | 9.4824e-08 | 0.00017896 | 0.0074009 | 0.0053588 | 8.2881e-05 | 0.0023313 | 1.0383e-33 | 1.2955e-06 | 0.00012806 | 0.017719 | 2.4808e-08 | 1.9158e-07 | 4.8439e-08 | 1.5868e-06 | 2.0815e-06 | 3.761e-06 | 0.0009397 | 0.0011911 | 0.0022426 | 2.4149e-09 | 4.7135e-05 | 2.7704e-09 | 6.0194e-07 | 7.2404e-09 | 5.5595e-07 | 2.2284e-07 | 1.5284e-07 | 1.6262e-07 | 1.6455e-07 | 1.1414e-06 | 1.5004e-06 | 0.00013324 | 6.9459e-05 | 9.735e-05 | 5.9702e-05 | 0.0006816 | 0.00052935 | 1.2176e-08 | 9.9308e-13 | 9.5334e-13 | 2.8561e-13 | 4.8339e-13 | 2.6202e-14 | 1.6943e-13 | 6.0404e-07 | 6.3257e-58 | 5.282e-59 | 4.5228e-60 | 1.5447e-59 | 9.7244e-61 | 1.1124e-58
5 | 5.2 | 5.2.3 | Variance | 0.0068629 | 0.008844 | 0.0068316 | 0.0014065 | 0.0010082 | 0.0013087 | 0.0070649 | 1.3171e-29 | 0.024954 | 0 | 0.010957 | 0 | 0.03255 | 2.1073e-28 | 0.0078211 | 0 | 0.019511 | 0 | 4.3798e-08 | 0.002482 | 3.8441e-08 | 0.00066234 | 7.3493e-08 | 0.00020068 | 0.0023223 | 0.0046678 | 0.00022013 | 0.0016068 | 5.3591e-34 | 1.443e-06 | 0.00018827 | 0.008844 | 6.159e-08 | 1.2157e-07 | 4.0432e-08 | 8.224e-07 | 1.1864e-06 | 1.5777e-06 | 0.00047868 | 0.00068184 | 0.00092664 | 2.962e-09 | 5.0032e-06 | 4.4066e-09 | 4.7889e-07 | 8.8636e-09 | 4.6503e-07 | 2.2963e-07 | 2.587e-07 | 1.9934e-07 | 2.4329e-07 | 2.2422e-06 | 2.9613e-06 | 0.00013763 | 9.3488e-05 | 0.00011912 | 8.6581e-05 | 0.001339 | 0.0010322 | 4.9914e-09 | 6.6024e-14 | 1.6887e-13 | 5.191e-14 | 1.0288e-13 | 1.2998e-13 | 4.6253e-13 | 2.4762e-07 | 4.4086e-59 | 1.1647e-59 | 9.4407e-61 | 4.0431e-60 | 4.9979e-60 | 3.0091e-58
5 | 5.3 | 5.3.1 | Variance | 0.15545 | 0.14937 | 0.21565 | 0.00045173 | 0.57742 | 0.58995 | 0.0074366 | 1.6463e-29 | 0.017996 | 0 | 0.0060359 | 0 | 0.016847 | 2.1073e-28 | 0.0037991 | 0 | 0.016953 | 0 | 6.9154e-07 | 0.00011093 | 5.997e-07 | 0.00019054 | 3.2948e-08 | 0.00011244 | 0.056557 | 0.030311 | 8.0868e-05 | 0.001259 | 5.895e-33 | 1.0413e-05 | 0.00011264 | 0.14937 | 2.7795e-06 | 1.2838e-07 | 1.8308e-07 | 3.0386e-05 | 3.5702e-05 | 2.5317e-05 | 0.017228 | 0.020985 | 0.014838 | 2.8963e-08 | 2.0351e-07 | 6.0837e-09 | 1.3137e-06 | 2.9593e-05 | 5.1886e-06 | 9.5952e-07 | 4.8062e-07 | 1.5922e-07 | 1.3337e-07 | 6.9184e-05 | 0.00011054 | 0.00055422 | 0.00017478 | 9.3519e-05 | 6.7863e-05 | 0.041246 | 0.036304 | 1.3736e-07 | 1.1248e-08 | 1.68e-08 | 7.5849e-08 | 6.0085e-10 | 4.4533e-10 | 2.2031e-10 | 6.7623e-06 | 5.5133e-07 | 8.3676e-07 | 3.4496e-06 | 1.7038e-54 | 8.9116e-55 | 6.1335e-55
5 | 5.3 | 5.3.2 | Variance | 0.017395 | 0.017847 | 0.027542 | 0.00060775 | 0.063526 | 0.061703 | 0.0096779 | 1.3171e-29 | 0.024652 | 0 | 0.0067221 | 0 | 0.017312 | 2.1073e-28 | 0.0054084 | 0 | 0.023503 | 0 | 2.8128e-07 | 0.00010941 | 1.4435e-07 | 0.00018648 | 4.7208e-08 | 0.00013397 | 0.01454 | 0.0023043 | 6.6348e-05 | 0.0016154 | 9.1105e-33 | 3.8059e-06 | 5.1221e-05 | 0.017847 | 4.8624e-06 | 5.2793e-08 | 5.8321e-08 | 6.3555e-06 | 3.2923e-06 | 8.4295e-06 | 0.0033939 | 0.0019223 | 0.0049407 | 1.8623e-09 | 5.2298e-07 | 3.2103e-09 | 1.1657e-06 | 1.7708e-05 | 8.2207e-07 | 2.021e-07 | 1.2707e-07 | 7.2525e-07 | 1.4723e-07 | 1.2853e-05 | 1.9149e-05 | 0.00011977 | 5.5385e-05 | 0.00042938 | 6.761e-05 | 0.0073449 | 0.0063936 | 3.3726e-08 | 4.9503e-09 | 1.1879e-08 | 5.3997e-09 | 9.1764e-11 | 3.2689e-12 | 7.9825e-12 | 1.6606e-06 | 2.4265e-07 | 5.9171e-07 | 2.4559e-07 | 1.3929e-55 | 1.0201e-56 | 2.6413e-56
5 | 5.3 | 5.3.3 | Variance | 0.043542 | 0.03696 | 0.050711 | 0.00093888 | 0.0058546 | 0.0049514 | 0.0067891 | 1.4817e-29 | 0.0187 | 0 | 0.0063757 | 0 | 0.019877 | 0 | 0.0073917 | 0 | 0.023083 | 0 | 3.351e-07 | 7.9906e-05 | 2.6076e-07 | 0.00010582 | 6.7884e-08 | 8.924e-05 | 0.0070509 | 0.018353 | 3.6686e-05 | 0.0012395 | 1.2862e-32 | 4.8316e-06 | 3.6634e-05 | 0.03696 | 8.771e-06 | 2.5383e-07 | 4.3099e-08 | 3.007e-06 | 6.4162e-06 | 4.2519e-06 | 0.0014797 | 0.0037169 | 0.0024873 | 1.7935e-09 | 1.8051e-07 | 3.7257e-09 | 9.3745e-06 | 2.8677e-07 | 2.5615e-06 | 2.7048e-07 | 1.3665e-07 | 2.2121e-07 | 3.9373e-07 | 3.7838e-05 | 6.2291e-05 | 0.00015918 | 4.8893e-05 | 0.00013052 | 0.00029166 | 0.022118 | 0.020329 | 8.7121e-09 | 3.2308e-09 | 5.0235e-09 | 4.3538e-09 | 4.1667e-10 | 3.7748e-12 | 6.1184e-12 | 4.2899e-07 | 1.5836e-07 | 2.5022e-07 | 1.9803e-07 | 5.8467e-55 | 1.1989e-56 | 1.8495e-56
5 | 5.4 | 5.4.1 | Variance | 1.8778 | 1.8237 | 0.062299 | 0.00066698 | 2.478 | 2.5389 | 0.0048668 | 1.4817e-29 | 0.020107 | 0 | 0.0086662 | 0 | 0.023104 | 2.1073e-28 | 0.0053112 | 0 | 0.013328 | 0 | 5.4558e-06 | 0.00038536 | 5.9298e-06 | 0.00011382 | 3.3466e-08 | 0.00017737 | 0.40893 | 0.55438 | 5.7272e-05 | 0.0016259 | 1.8757e-32 | 8.3272e-05 | 0.00046192 | 1.8237 | 3.561e-06 | 7.0066e-08 | 5.1313e-08 | 1.4994e-05 | 1.8192e-05 | 1.5887e-05 | 0.0084031 | 0.010611 | 0.009272 | 2.1406e-08 | 2.3725e-06 | 1.9192e-08 | 6.0123e-06 | 3.7433e-08 | 4.5137e-06 | 4.174e-07 | 9.6674e-07 | 2.7325e-07 | 2.5688e-07 | 1.3613e-05 | 4.2953e-05 | 0.00024544 | 0.0004793 | 0.0001639 | 4.8612e-05 | 0.0078374 | 0.014479 | 1.1883e-07 | 4.701e-08 | 4.4345e-08 | 1.4587e-07 | 2.1462e-07 | 4.5078e-08 | 1.8686e-07 | 5.81e-06 | 2.2882e-06 | 2.1937e-06 | 6.586e-06 | 1.0124e-05 | 1.9203e-06 | 8.3878e-06
5 | 5.4 | 5.4.2 | Variance | 0.19804 | 0.21263 | 0.041571 | 0.0010333 | 0.40949 | 0.38569 | 0.017516 | 1.6463e-29 | 0.055802 | 0 | 0.014147 | 0 | 0.029682 | 1.4049e-28 | 0.012569 | 0 | 0.047232 | 0 | 3.0278e-06 | 0.00046403 | 2.4852e-06 | 0.00034327 | 9.2947e-08 | 0.00017749 | 0.065044 | 0.049116 | 2.8489e-05 | 0.0034994 | 1.2862e-32 | 4.5355e-05 | 0.00025823 | 0.21263 | 9.6889e-06 | 3.9799e-08 | 3.3854e-08 | 6.01e-06 | 4.7493e-06 | 4.2583e-06 | 0.0036559 | 0.0027632 | 0.0024784 | 4.128e-08 | 1.0876e-06 | 3.001e-08 | 5.7594e-07 | 3.0047e-06 | 2.5433e-06 | 4.5816e-07 | 3.1515e-07 | 3.9618e-07 | 6.5432e-07 | 1.2426e-05 | 1.8336e-05 | 0.00025226 | 0.00017491 | 0.00024497 | 0.00029391 | 0.0071819 | 0.0053993 | 4.973e-08 | 5.6132e-09 | 5.4685e-09 | 7.4358e-09 | 1.1018e-08 | 1.0538e-08 | 2.1133e-07 | 2.4312e-06 | 2.7322e-07 | 2.7053e-07 | 3.3576e-07 | 5.1978e-07 | 4.4891e-07 | 9.4866e-06
5 | 5.4 | 5.4.3 | Variance | 0.07469 | 0.075212 | 0.0012408 | 0.0011808 | 0.088033 | 0.086353 | 0.014557 | 1.4817e-29 | 0.04679 | 0 | 0.012713 | 3.5121e-29 | 0.027468 | 1.4049e-28 | 0.0091936 | 0 | 0.035146 | 0 | 1.7491e-06 | 0.00037133 | 1.2517e-06 | 0.00019149 | 8.2924e-08 | 0.00020399 | 0.032706 | 0.017377 | 5.1213e-05 | 0.0033657 | 1.6077e-32 | 2.389e-05 | 0.00046759 | 0.075212 | 3.4462e-06 | 7.4779e-09 | 1.6226e-08 | 9.5039e-07 | 5.86e-07 | 2.2534e-06 | 0.00050753 | 0.00034118 | 0.0013119 | 5.2611e-09 | 5.6018e-08 | 9.4582e-09 | 4.6989e-07 | 1.8814e-08 | 3.3015e-07 | 2.028e-07 | 2.3357e-07 | 3.6494e-07 | 2.41e-07 | 4.5274e-06 | 5.7338e-06 | 0.00011664 | 7.5958e-05 | 0.00021608 | 0.0001109 | 0.0025981 | 0.0020221 | 1.9294e-08 | 7.0348e-09 | 7.6416e-09 | 1.7968e-08 | 8.736e-09 | 8.8225e-09 | 1.4519e-07 | 9.4317e-07 | 3.4241e-07 | 3.7801e-07 | 8.1126e-07 | 4.1213e-07 | 3.7583e-07 | 6.5168e-06
6 | 6.1 | 6.1.1 | Variance | 0.0024065 | 0.0004886 | 0.0027218 | 0.0022364 | 0.0026858 | 0.005597 | 0.011216 | 1.4817e-29 | 0.041039 | 0 | 0.015526 | 0 | 0.038608 | 8.7804e-29 | 0.0079877 | 0 | 0.024563 | 0 | 1.5127e-07 | 0.00035513 | 3.271e-07 | 0.0015447 | 1.9074e-07 | 0.019399 | 0.004013 | 0.00053583 | 0.00080885 | 0.0045577 | 0 | 1.9213e-07 | 8.1656e-05 | 0.0004886 | 8.8031e-09 | 6.755e-09 | 1.9349e-08 | 0 | 0 | 0 | 1.5736e-13 | 1.0038e-13 | 6.4577e-13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.318e-05 | 7.701e-06 | 0 | 0 | 0 | 0 | 0.032182 | 0.0027218 | 4.7854e-14 | 5.6475e-14 | 6.2969e-14 | 9.7817e-14 | 1.2157e-13 | 1.0781e-13 | 7.5209e-14 | 5.2765e-63 | 2.7407e-63 | 1.2173e-63 | 2.9458e-64 | 2.9e-62 | 1.5345e-63 | 7.8122e-64
6 | 6.1 | 6.1.2 | Variance | 0.0030665 | 0.00047465 | 1.0272e-05 | 0.0025488 | 0.00047627 | 0.0031844 | 0.01177 | 1.3171e-29 | 0.037057 | 0 | 0.014981 | 0 | 0.041065 | 2.1073e-28 | 0.012789 | 0 | 0.040529 | 0 | 1.3777e-07 | 0.00034898 | 2.4401e-07 | 0.000894 | 3.2761e-07 | 0.034974 | 0.0041593 | 0.00019447 | 0.00027242 | 0.0073102 | 0 | 2.4526e-07 | 0.0001221 | 0.00047465 | 6.7603e-09 | 4.4239e-09 | 4.25e-08 | 0 | 0 | 0 | 1.1026e-13 | 1.1575e-13 | 4.3278e-13 | 2.0434e-09 | 3.0158e-07 | 4.5519e-09 | 2.8608e-07 | 4.6254e-09 | 2.8373e-07 | 2.236e-08 | 8.3137e-09 | 3.0864e-08 | 4.7587e-09 | 2.8528e-08 | 2.1082e-08 | 1.3476e-05 | 2.964e-06 | 1.8609e-05 | 1.6748e-06 | 1.7205e-05 | 7.4605e-06 | 3.684e-14 | 4.0752e-14 | 6.2637e-14 | 3.2092e-14 | 9.951e-14 | 4.2923e-14 | 9.6205e-14 | 3.8197e-63 | 3.5484e-63 | 1.9768e-63 | 8.8371e-64 | 3.1821e-62 | 1.1827e-63 | 7.3517e-64
6 | 6.1 | 6.1.3 | Variance | 0.0025958 | 0.00041474 | 1.1105e-05 | 0.0018849 | 0.00047266 | 0.0026631 | 0.011117 | 1.7561e-29 | 0.029351 | 0 | 0.0083732 | 0 | 0.024575 | 7.0243e-29 | 0.009513 | 0 | 0.033076 | 0 | 1.215e-07 | 0.00029828 | 2.0149e-07 | 0.00039048 | 2.3534e-07 | 0.022579 | 0.0036909 | 0.00022052 | 0.00024902 | 0.0054278 | 0 | 1.416e-07 | 8.5914e-05 | 0.00041474 | 8.082e-09 | 2.3224e-09 | 1.1164e-08 | 0 | 0 | 0 | 1.9844e-13 | 1.1106e-13 | 6.3062e-13 | 2.9065e-09 | 1.9564e-07 | 2.9953e-09 | 2.68e-07 | 3.7129e-09 | 2.0785e-07 | 3.2409e-08 | 8.7306e-09 | 3.1217e-08 | 1.1374e-08 | 3.0478e-08 | 9.3497e-09 | 1.9534e-05 | 3.1074e-06 | 1.8819e-05 | 3.9953e-06 | 1.8378e-05 | 3.3203e-06 | 5.7616e-14 | 4.7574e-14 | 4.3431e-14 | 3.9792e-14 | 5.0435e-14 | 5.2543e-14 | 7.9384e-14 | 7.6112e-63 | 4.3759e-63 | 1.58e-63 | 1.2446e-63 | 1.5567e-62 | 1.5048e-63 | 3.7857e-64
6 | 6.2 | 6.2.1 | Variance | 0.23479 | 0.24338 | 0.11044 | 0.00099903 | 0.042308 | 0.042071 | 0.0074485 | 1.9207e-29 | 0.02511 | 0 | 0.01039 | 0 | 0.03394 | 3.5121e-29 | 0.0099758 | 0 | 0.024403 | 0 | 9.907e-07 | 0.058652 | 2.4358e-06 | 0.38902 | 4.1006e-06 | 0.24001 | 0.54948 | 0.37119 | 0.12063 | 0.0057292 | 0 | 8.0892e-05 | 0.070342 | 0.24338 | 2.6483e-06 | 8.3652e-07 | 8.9289e-07 | 2.1125e-05 | 1.4369e-05 | 2.392e-05 | 0.012095 | 0.008689 | 0.014414 | 1.2929e-06 | 9.0457e-08 | 1.2927e-06 | 9.2199e-06 | 1.2571e-06 | 4.1214e-08 | 6.7302e-07 | 2.0072e-07 | 1.589e-07 | 1.3299e-07 | 2.2881e-07 | 1.0908e-07 | 0.00039328 | 7.0535e-05 | 9.7436e-05 | 4.8088e-05 | 0.00013037 | 3.8277e-05 | 2.185e-06 | 3.1332e-10 | 1.6995e-11 | 3.5994e-12 | 8.1233e-12 | 1.4274e-11 | 3.0933e-10 | 0.00010829 | 6.0271e-56 | 9.4249e-59 | 3.6987e-60 | 5.2574e-60 | 6.0468e-59 | 1.2711e-55
6 | 6.2 | 6.2.2 | Variance | 0.044747 | 0.046791 | 0.049276 | 0.0022312 | 0.00021822 | 0.002161 | 0.0093045 | 1.3171e-29 | 0.035525 | 0 | 0.013378 | 0 | 0.039469 | 9.6584e-29 | 0.009887 | 0 | 0.022721 | 0 | 1.4147e-07 | 0.00044589 | 7.5586e-08 | 0.060457 | 5.4608e-07 | 0.0014555 | 0.011047 | 0.0016504 | 0.022055 | 0.0057214 | 0 | 2.3962e-06 | 0.00035931 | 0.046791 | 1.3323e-06 | 8.9929e-08 | 1.609e-07 | 1.8206e-05 | 2.4252e-07 | 2.4972e-05 | 0.010433 | 0.00014291 | 0.01475 | 1.4791e-09 | 2.0075e-08 | 2.5213e-09 | 6.6605e-07 | 2.6957e-09 | 7.1194e-08 | 3.8707e-07 | 1.2671e-07 | 1.7737e-07 | 9.5092e-08 | 8.6244e-08 | 1.2166e-07 | 0.00023157 | 4.4364e-05 | 0.00010618 | 3.2805e-05 | 5.1629e-05 | 4.3078e-05 | 3.0235e-08 | 5.3938e-13 | 1.0197e-12 | 5.7424e-14 | 3.1038e-13 | 9.7546e-13 | 8.7678e-13 | 1.4987e-06 | 2.5959e-58 | 3.2099e-59 | 4.1038e-61 | 3.6851e-60 | 6.9424e-60 | 6.0746e-58
6 | 6.2 | 6.2.3 | Variance | 0.031451 | 0.027378 | 0.023963 | 0.00097425 | 0.00050011 | 0.0016183 | 0.0046429 | 2.0853e-29 | 0.014144 | 0 | 0.0051759 | 0 | 0.018864 | 1.4049e-28 | 0.0059522 | 0 | 0.014299 | 0 | 8.6074e-08 | 0.00017818 | 7.1244e-08 | 0.030198 | 1.0674e-07 | 0.00052562 | 0.0036877 | 0.001359 | 0.011661 | 0.0033512 | 0 | 4.4589e-07 | 0.0001484 | 0.027378 | 1.4273e-07 | 6.2168e-08 | 6.8718e-08 | 5.8021e-06 | 2.6165e-06 | 7.4e-06 | 0.0034365 | 0.0015526 | 0.0043724 | 1.3301e-09 | 3.0344e-08 | 2.0063e-09 | 9.9633e-06 | 1.354e-09 | 4.3811e-08 | 5.2103e-07 | 9.3802e-08 | 2.337e-07 | 5.0896e-07 | 1.1371e-07 | 1.9184e-07 | 0.00031185 | 3.3104e-05 | 0.0001399 | 0.00016973 | 6.7993e-05 | 6.7227e-05 | 6.113e-08 | 8.4754e-13 | 4.4118e-13 | 1.7897e-13 | 2.8864e-13 | 2.2293e-13 | 1.2043e-12 | 3.0305e-06 | 4.1329e-58 | 1.5342e-59 | 8.3286e-61 | 3.7397e-60 | 6.1578e-61 | 8.2805e-58
6 | 6.3 | 6.3.1 | Variance | 0.19259 | 0.17778 | 0.093344 | 0.0022562 | 0.33765 | 0.35778 | 0.014929 | 1.3171e-29 | 0.042369 | 0 | 0.013952 | 0 | 0.04318 | 2.1073e-28 | 0.014821 | 0 | 0.045558 | 0 | 3.5267e-07 | 7.8179e-05 | 9.0086e-07 | 0.00030918 | 1.9173e-06 | 0.00016431 | 0.020213 | 0.0036192 | 0.089174 | 0.0087644 | 0 | 6.0788e-06 | 0.00032098 | 0.17778 | 0.0015489 | 5.3147e-08 | 9.8289e-08 | 5.9803e-05 | 2.6627e-05 | 1.7261e-05 | 0.052992 | 0.015667 | 0.010125 | 2.6489e-09 | 1.8045e-06 | 2.3735e-09 | 2.017e-05 | 4.6155e-07 | 2.8206e-06 | 1.8095e-07 | 4.3063e-07 | 9.4378e-07 | 4.5912e-07 | 1.7201e-05 | 2.7265e-05 | 0.00010729 | 0.000215 | 0.00055814 | 0.00041472 | 0.0099787 | 0.0087514 | 4.5722e-08 | 1.2389e-08 | 1.4718e-08 | 7.4187e-08 | 8.1651e-10 | 6.6768e-10 | 5.17e-10 | 2.2515e-06 | 6.0731e-07 | 7.3313e-07 | 3.3742e-06 | 9.4038e-55 | 1.2203e-54 | 1.2174e-54
6 | 6.3 | 6.3.2 | Variance | 0.20535 | 0.18373 | 0.25287 | 0.001359 | 0.024671 | 0.025789 | 0.0084105 | 1.7561e-29 | 0.021957 | 0 | 0.0057526 | 0 | 0.017384 | 2.1073e-28 | 0.0073446 | 0 | 0.025175 | 0 | 4.1813e-07 | 3.8843e-05 | 3.0585e-07 | 0.00022359 | 1.0897e-06 | 2.3736e-05 | 0.018256 | 0.0045914 | 0.083797 | 0.0043082 | 0 | 4.0124e-06 | 0.00027485 | 0.18373 | 0.0018031 | 1.7262e-08 | 7.5193e-08 | 0.00011358 | 3.058e-06 | 5.3692e-06 | 0.095268 | 0.001797 | 0.0031372 | 7.968e-09 | 2.8907e-07 | 6.151e-09 | 4.1893e-07 | 8.8289e-07 | 4.329e-06 | 1.6035e-07 | 1.3942e-07 | 2.2702e-07 | 1.8649e-07 | 6.8116e-05 | 0.00010243 | 9.4266e-05 | 5.284e-05 | 0.0001336 | 6.2206e-05 | 0.039878 | 0.033314 | 1.0732e-08 | 1.3223e-08 | 9.1586e-09 | 9.5607e-09 | 6.7623e-11 | 1.1173e-11 | 5.8963e-12 | 5.285e-07 | 6.4816e-07 | 4.5621e-07 | 4.3487e-07 | 7.2884e-56 | 2.9749e-56 | 1.7566e-56
6 | 6.3 | 6.3.3 | Variance | 0.0031883 | 0.0016529 | 0.0024805 | 0.0023133 | 0.0015722 | 0.0045798 | 0.014571 | 1.3171e-29 | 0.044267 | 0 | 0.014548 | 0 | 0.045462 | 2.1073e-28 | 0.016075 | 0 | 0.045859 | 0 | 3.8995e-08 | 6.3767e-05 | 6.612e-07 | 0.00046257 | 6.3297e-07 | 0.00010445 | 0.0092357 | 0.0027229 | 0.0011056 | 0.0094892 | 0 | 1.5072e-06 | 0.00027702 | 0.0016529 | 4.6955e-05 | 3.176e-08 | 1.5116e-08 | 1.3539e-07 | 4.0365e-07 | 2.4339e-06 | 0.00027167 | 0.00024186 | 0.0014271 | 4.1137e-09 | 6.1368e-07 | 2.3083e-09 | 2.06e-08 | 2.5633e-07 | 5.8507e-07 | 1.4683e-07 | 1.4996e-07 | 2.8438e-07 | 2.0209e-07 | 1.0062e-06 | 2.8475e-06 | 8.7576e-05 | 6.5877e-05 | 0.00016819 | 6.61e-05 | 0.00062218 | 0.00092828 | 4.5831e-09 | 2.9388e-09 | 3.8675e-09 | 2.5912e-09 | 1.0782e-11 | 4.0304e-12 | 1.9674e-12 | 2.257e-07 | 1.4405e-07 | 1.9265e-07 | 1.1786e-07 | 6.4714e-57 | 1.0318e-56 | 5.4157e-57
6 | 6.4 | 6.4.1 | Variance | 3.3778 | 3.3135 | 0.18546 | 0.0012762 | 4.7221 | 4.7887 | 0.015603 | 1.3171e-29 | 0.064196 | 0 | 0.028181 | 0 | 0.085792 | 2.1073e-28 | 0.021317 | 0 | 0.045428 | 0 | 5.6591e-06 | 0.00010243 | 1.0866e-05 | 0.00013889 | 3.219e-05 | 8.9313e-05 | 0.078441 | 0.088704 | 1.6268 | 0.012941 | 0 | 0.00011409 | 0.0012068 | 3.3135 | 5.6052e-06 | 3.0928e-07 | 2.3538e-07 | 3.4788e-05 | 4.7443e-05 | 3.6845e-05 | 0.019348 | 0.027629 | 0.021464 | 1.9106e-07 | 4.1923e-05 | 7.1187e-08 | 7.4302e-05 | 2.2468e-06 | 1.4153e-05 | 1.0579e-05 | 6.0645e-06 | 1.7721e-06 | 2.842e-06 | 9.4705e-05 | 0.00014652 | 0.0059562 | 0.0050044 | 0.0010747 | 0.0039067 | 0.053182 | 0.04936 | 2.7434e-06 | 4.1913e-08 | 6.6329e-08 | 6.9961e-08 | 5.0636e-07 | 4.6992e-07 | 4.1962e-07 | 0.00013413 | 2.0401e-06 | 3.2808e-06 | 3.1586e-06 | 2.3885e-05 | 2.0023e-05 | 1.8836e-05
6 | 6.4 | 6.4.2 | Variance | 0.22769 | 0.18696 | 0.043988 | 0.0079777 | 0.20788 | 0.23497 | 0.011466 | 1.7561e-29 | 0.029187 | 0 | 0.0077214 | 0 | 0.022542 | 1.0536e-28 | 0.0088645 | 0 | 0.03244 | 0 | 4.503e-07 | 0.00010462 | 1.0064e-06 | 0.00015498 | 2.5588e-06 | 5.1954e-05 | 0.02176 | 0.012767 | 0.10556 | 0.0063674 | 0 | 8.9585e-06 | 0.00012923 | 0.18696 | 4.9144e-06 | 1.3827e-07 | 2.0055e-07 | 1.0542e-05 | 8.2508e-06 | 9.185e-06 | 0.0057456 | 0.004781 | 0.005313 | 1.2141e-07 | 2.9264e-06 | 1.0916e-07 | 4.5783e-07 | 1.2304e-07 | 3.0722e-06 | 1.3014e-06 | 4.8232e-07 | 2.5012e-07 | 2.5122e-07 | 9.1979e-06 | 1.5007e-05 | 0.00071278 | 0.00033086 | 0.00016325 | 0.00012181 | 0.0052616 | 0.0046534 | 2.7867e-07 | 3.5945e-08 | 7.3966e-09 | 3.5125e-08 | 5.4775e-08 | 1.3602e-06 | 6.6686e-08 | 1.3626e-05 | 1.7496e-06 | 3.6587e-07 | 1.5858e-06 | 2.5839e-06 | 5.7956e-05 | 2.993e-06
6 | 6.4 | 6.4.3 | Variance | 0.031441 | 0.016113 | 0.017428 | 0.0058165 | 0.016959 | 0.024011 | 0.010342 | 1.9207e-29 | 0.031139 | 0 | 0.010516 | 0 | 0.027281 | 3.5121e-29 | 0.0073783 | 0 | 0.026304 | 0 | 8.0585e-08 | 0.00019141 | 5.8101e-07 | 0.00032392 | 9.9317e-07 | 6.2589e-05 | 0.0098277 | 0.015618 | 0.01505 | 0.0046733 | 0 | 3.1522e-06 | 0.00010297 | 0.016113 | 7.7329e-06 | 5.9636e-08 | 5.4169e-08 | 2.0293e-06 | 7.4529e-06 | 3.8411e-06 | 0.00097038 | 0.0043328 | 0.0022267 | 2.9257e-08 | 1.3881e-06 | 2.076e-08 | 3.4722e-07 | 1.405e-07 | 1.2111e-06 | 2.6516e-07 | 1.9797e-07 | 2.3774e-07 | 9.4717e-08 | 1.8442e-05 | 2.4428e-05 | 0.00014612 | 6.3689e-05 | 0.00014563 | 4.0249e-05 | 0.010505 | 0.0078463 | 5.838e-08 | 8.0463e-09 | 3.144e-09 | 5.8584e-09 | 1.8098e-07 | 8.3306e-08 | 7.8998e-09 | 2.8541e-06 | 3.9163e-07 | 1.5552e-07 | 2.6449e-07 | 8.5372e-06 | 3.5488e-06 | 3.5453e-07
5 | 5.1 | All | Variance | 0.0024278 | 0.00058869 | 3.0678e-05 | 0.00074019 | 0.00038484 | 0.0019235 | 0.0082345 | 0 | 0.034181 | 0 | 0.013557 | 0 | 0.035465 | 1.5612e-05 | 0.0096738 | 0 | 0.025261 | 0.00027086 | 1.0439e-07 | 0.00038755 | 1.0917e-07 | 0.0021697 | 5.6129e-08 | 0.0016918 | 0.00011253 | 0.00042378 | 0.0011359 | 0.0021927 | 1.2821e-07 | 6.9122e-10 | 0.0010382 | 0.00058869 | 8.6624e-08 | 6.4091e-09 | 6.8002e-08 | 0 | 0 | 0 | 7.629e-14 | 2.5021e-14 | 7.3715e-13 | 1.6028e-07 | 2.9814e-05 | 1.6357e-07 | 4.1702e-05 | 1.6166e-07 | 3.6254e-05 | 7.499e-07 | 5.0373e-08 | 1.5382e-08 | 7.6338e-09 | 6.5432e-07 | 7.3271e-09 | 0.00045302 | 1.823e-05 | 9.328e-06 | 2.8176e-06 | 0.00039535 | 2.5164e-06 | 1.0635e-14 | 1.4908e-14 | 2.2417e-14 | 4.7575e-15 | 2.4764e-14 | 3.0943e-14 | 7.6329e-14 | 1.8223e-63 | 1.6778e-63 | 6.2014e-64 | 5.7131e-65 | 5.6899e-63 | 3.5044e-64 | 5.3146e-64
5 | 5.2 | All | Variance | 0.81588 | 0.91858 | 0.84574 | 0.0030429 | 0.0069799 | 0.005415 | 0.00046472 | 0 | 0.0025261 | 0 | 0.012463 | 0 | 0.084672 | 0.0014164 | 0.019197 | 0 | 0.0066955 | 0.00010143 | 3.4741e-06 | 0.013432 | 3.1974e-06 | 0.0063856 | 7.9378e-08 | 7.6618e-06 | 0.19466 | 0.23118 | 0.00036884 | 0.00030648 | 1.1513e-06 | 8.5195e-05 | 0.0024249 | 0.91858 | 6.8559e-07 | 6.4483e-06 | 1.4136e-06 | 0.00019566 | 0.00014422 | 0.00018041 | 0.11577 | 0.083152 | 0.10573 | 3.5463e-09 | 4.9412e-05 | 5.8638e-09 | 3.2245e-05 | 7.4878e-09 | 2.6357e-05 | 1.9935e-07 | 2.1092e-09 | 2.0703e-07 | 3.3402e-07 | 4.2862e-06 | 5.4941e-06 | 0.00011903 | 8.9754e-06 | 0.00012446 | 0.00014694 | 0.002563 | 0.00199 | 1.1563e-07 | 9.9167e-11 | 5.6544e-11 | 2.5772e-11 | 0.0011025 | 8.5474e-12 | 1.614e-12 | 5.7363e-06 | 5.418e-56 | 2.4435e-57 | 2.4953e-58 | 1.2203e-42 | 2.5726e-58 | 9.8546e-58
5 | 5.3 | All | Variance | 0.35554 | 0.36301 | 1.4889 | 0.0030152 | 3.0878 | 2.9908 | 0.02193 | 0 | 0.069073 | 0 | 0.01431 | 0 | 0.023716 | 0.00046894 | 0.0038613 | 0 | 0.027484 | 6.1358e-05 | 1.5126e-06 | 0.0015392 | 9.6839e-07 | 0.0011219 | 1.3415e-07 | 0.0009998 | 0.16783 | 0.029645 | 0.00052158 | 0.0039406 | 2.561e-06 | 1.6939e-05 | 0.0016431 | 0.36301 | 0.00019124 | 3.6236e-06 | 2.2504e-06 | 0.00035806 | 0.00040256 | 0.00037918 | 0.19479 | 0.23575 | 0.22234 | 4.957e-09 | 4.6947e-06 | 7.2935e-10 | 5.4922e-05 | 9.1513e-07 | 2.2527e-05 | 1.3142e-05 | 8.0756e-08 | 2.0339e-06 | 2.4716e-06 | 3.2123e-05 | 7.3802e-05 | 0.0077402 | 2.6517e-05 | 0.0012061 | 0.0019748 | 0.018907 | 0.027992 | 1.15e-06 | 8.5476e-08 | 7.1733e-08 | 2.7566e-07 | 2.6017e-09 | 8.3479e-10 | 9.5767e-11 | 5.6623e-05 | 4.1897e-06 | 3.573e-06 | 1.2537e-05 | 5.3442e-54 | 2.0646e-54 | 2.8307e-55
5 | 5.4 | All | Variance | 6.252 | 6.9545 | 1.0212 | 0.050069 | 12.9826 | 11.8897 | 0.024545 | 0 | 0.022771 | 0 | 0.0032501 | 0 | 0.0094228 | 0.00067143 | 0.016569 | 0 | 0.101 | 0.00023784 | 1.8955e-05 | 0.003164 | 1.8503e-05 | 0.00049957 | 1.5268e-07 | 0.00069925 | 2.2098 | 1.0534 | 0.00065084 | 0.0045606 | 3.8866e-08 | 0.00025423 | 0.0053089 | 6.9545 | 0.00017071 | 1.7043e-06 | 2.0022e-06 | 0.00014542 | 0.0002475 | 0.00022896 | 0.074828 | 0.14402 | 0.13308 | 1.1168e-06 | 3.0221e-05 | 7.7815e-07 | 2.2437e-06 | 1.2367e-05 | 8.9821e-05 | 7.2612e-06 | 2.0509e-06 | 2.7926e-06 | 3.8517e-06 | 5.2088e-06 | 2.0511e-06 | 0.0037798 | 0.0022327 | 0.0018366 | 0.0013659 | 0.0019259 | 0.00012895 | 1.1296e-06 | 6.874e-08 | 9.8259e-08 | 3.7856e-07 | 3.2372e-07 | 9.0026e-08 | 7.1969e-07 | 5.5222e-05 | 3.3458e-06 | 4.8608e-06 | 1.7093e-05 | 1.5271e-05 | 3.8351e-06 | 3.2305e-05
6 | 6.1 | All | Variance | 0.0048379 | 0.00060358 | 0.019568 | 0.0021113 | 0.0133 | 0.0053594 | 0.0020564 | 0 | 0.00073714 | 0 | 0.0010203 | 0 | 0.004073 | 0.00013016 | 0.00046758 | 0 | 0.0058157 | 2.5111e-05 | 6.8638e-09 | 0.00032748 | 1.0393e-07 | 0.00030805 | 5.4384e-08 | 0.009592 | 0.00021428 | 0.00028301 | 0.0027792 | 0.00026655 | 8.1193e-05 | 2.2122e-07 | 0.00019611 | 0.00060358 | 1.6487e-07 | 5.6683e-08 | 4.2634e-07 | 0 | 0 | 0 | 7.4679e-16 | 2.753e-15 | 2.0976e-13 | 0.00077558 | 0.00062216 | 0.00076738 | 0.00065079 | 0.00077826 | 0.00041066 | 4.0742e-05 | 7.6508e-07 | 1.7677e-05 | 3.0373e-06 | 3.357e-05 | 4.32e-05 | 0.024343 | 0.00026813 | 0.010858 | 0.0010849 | 0.020647 | 0.015207 | 3.4687e-14 | 1.1339e-14 | 2.7161e-14 | 1.4554e-13 | 2.8622e-14 | 2.9928e-14 | 5.7679e-15 | 4.2336e-63 | 7.8278e-64 | 6.8423e-64 | 1.1378e-63 | 7.9062e-63 | 4.0077e-64 | 4.6432e-65
6 | 6.2 | All | Variance | 2.4122 | 2.2069 | 2.4583 | 0.005384 | 0.0082817 | 0.0049925 | 0.01118 | 0 | 0.041343 | 0 | 0.032105 | 0 | 0.15796 | 0.00024033 | 0.047536 | 0 | 0.07314 | 0.00011745 | 4.0089e-06 | 0.01785 | 2.0085e-05 | 0.05953 | 6.1611e-06 | 0.40861 | 0.63867 | 0.059959 | 0.96336 | 0.024893 | 0.0004909 | 6.591e-05 | 0.016104 | 2.2069 | 2.0772e-06 | 2.3477e-06 | 2.8335e-06 | 0.00048917 | 0.00016556 | 0.00085289 | 0.28608 | 0.097338 | 0.50468 | 1.26e-07 | 1.1634e-06 | 1.603e-07 | 8.8312e-06 | 3.0892e-07 | 2.2037e-06 | 1.4976e-06 | 1.287e-07 | 3.1615e-08 | 5.3137e-08 | 4.7802e-07 | 8.6793e-08 | 0.00088931 | 4.0951e-05 | 1.8871e-05 | 1.0889e-05 | 0.00027945 | 3.5555e-05 | 3.7449e-06 | 3.4977e-10 | 8.1199e-11 | 1.549e-11 | 5.3237e-11 | 5.2256e-12 | 1.412e-10 | 0.00018563 | 1.051e-55 | 1.2567e-57 | 4.744e-59 | 2.2713e-58 | 2.5043e-59 | 7.0315e-56
6 | 6.3 | All | Variance | 0.056123 | 0.068658 | 1.7042 | 0.0021467 | 1.9349 | 1.9986 | 0.017466 | 0 | 0.060175 | 0 | 0.017986 | 0 | 0.036685 | 0.00029555 | 0.0092832 | 0 | 0.037357 | 0.00014703 | 5.4458e-08 | 4.7857e-05 | 7.9814e-07 | 0.0010468 | 1.2912e-06 | 0.0002605 | 0.003255 | 0.011479 | 0.035654 | 0.0059325 | 0.00035003 | 3.8819e-06 | 0.001528 | 0.068658 | 0.00039795 | 1.9797e-07 | 1.5668e-06 | 0.00043176 | 0.00018242 | 0.00026292 | 0.27484 | 0.10747 | 0.15414 | 3.7593e-09 | 5.4735e-06 | 1.5811e-08 | 5.7589e-06 | 5.1049e-07 | 3.8118e-05 | 2.5992e-06 | 1.9677e-07 | 5.7506e-08 | 2.6986e-08 | 1.5132e-05 | 1.9223e-05 | 0.0015262 | 0.00017979 | 3.6738e-05 | 5.8685e-06 | 0.0091048 | 0.0045171 | 4.8039e-08 | 2.5058e-08 | 1.8326e-08 | 2.7523e-07 | 8.4356e-10 | 2.5485e-10 | 6.4323e-11 | 2.3656e-06 | 1.2283e-06 | 9.1282e-07 | 1.2518e-05 | 8.3988e-55 | 5.3033e-55 | 1.5903e-55
6 | 6.4 | All | Variance | 3.3218 | 5.7238 | 1.7817 | 0.32595 | 13.7277 | 9.861 | 0.019726 | 0 | 0.079225 | 0 | 0.036705 | 0 | 0.1262 | 0.00030878 | 0.036562 | 0 | 0.073393 | 0.00060358 | 5.7219e-06 | 1.1977e-05 | 6.4708e-06 | 0.00048838 | 2.378e-05 | 0.00044014 | 0.19403 | 0.033475 | 1.4626 | 0.035728 | 0.00044252 | 8.8811e-05 | 0.0019795 | 5.7238 | 3.298e-05 | 4.551e-06 | 5.9693e-06 | 0.00048448 | 0.00056251 | 0.00048974 | 0.27302 | 0.32708 | 0.28422 | 3.197e-06 | 0.00010205 | 1.931e-06 | 5.4906e-05 | 6.854e-06 | 8.421e-05 | 7.1385e-05 | 1.3722e-05 | 2.811e-06 | 4.7684e-06 | 0.00011198 | 0.00020004 | 0.039268 | 0.011697 | 0.0020263 | 0.0046971 | 0.061036 | 0.085099 | 1.0128e-06 | 1.5666e-07 | 3.6904e-08 | 1.0083e-07 | 2.9563e-07 | 1.6348e-06 | 2.3333e-06 | 4.9518e-05 | 7.6254e-06 | 1.8254e-06 | 4.5524e-06 | 1.3945e-05 | 6.9649e-05 | 0.00010473
5 | 5.1 | 5.1.1 | Standard Deviation | 0.043796 | 0.016796 | 0.0023021 | 0.043572 | 0.017677 | 0.043047 | 0.087979 | 4.0575e-15 | 0.19221 | 0 | 0.12122 | 0 | 0.18022 | 8.8895e-15 | 0.082896 | 0 | 0.13614 | 0 | 0.00036481 | 0.010548 | 0.00046421 | 0.029015 | 0.00030401 | 0.020471 | 0.032542 | 0.026944 | 0.015575 | 0.048382 | 6.9389e-18 | 0.00022473 | 0.021936 | 0.016796 | 9.5669e-05 | 6.4804e-05 | 7.1005e-05 | 0 | 0 | 0 | 6.4142e-07 | 4.6764e-07 | 5.6363e-07 | 9.0095e-05 | 0.00085299 | 8.81e-05 | 0.00091354 | 9.443e-05 | 0.00086476 | 0.00031292 | 8.4809e-05 | 0.00019614 | 7.693e-05 | 0.00029808 | 0.00013297 | 0.0076854 | 0.0016047 | 0.0048132 | 0.0014445 | 0.0073222 | 0.0024985 | 2.377e-07 | 2.0092e-07 | 2.1112e-07 | 2.2358e-07 | 1.9184e-07 | 1.8465e-07 | 1.6083e-07 | 1.0644e-31 | 6.1706e-32 | 4.1076e-32 | 3.1393e-32 | 8.9646e-32 | 3.1648e-32 | 2.1833e-32
5 | 5.1 | 5.1.2 | Standard Deviation | 0.035243 | 0.010859 | 0.0026057 | 0.032572 | 0.010896 | 0.035367 | 0.090022 | 4.1906e-15 | 0.13992 | 0 | 0.078355 | 0 | 0.1412 | 9.3704e-15 | 0.081397 | 0 | 0.15204 | 0 | 0.00028353 | 0.010055 | 0.00027165 | 0.023768 | 0.00022519 | 0.0084939 | 0.025082 | 0.023725 | 0.0058903 | 0.035205 | 6.3067e-18 | 0.00020811 | 0.012921 | 0.010859 | 8.3456e-05 | 5.3067e-05 | 6.9389e-05 | 0 | 0 | 0 | 4.2876e-07 | 4.5743e-07 | 6.5287e-07 | 6.2723e-05 | 0.0004371 | 5.7544e-05 | 0.00067317 | 6.0472e-05 | 0.00048504 | 0.00027356 | 8.3802e-05 | 0.00023683 | 9.2511e-05 | 0.0001598 | 9.64e-05 | 0.0067174 | 0.0015801 | 0.0058146 | 0.0017376 | 0.0039242 | 0.0018144 | 1.9496e-07 | 2.2995e-07 | 2.5186e-07 | 3.0597e-07 | 2.7423e-07 | 2.5819e-07 | 1.8276e-07 | 7.1468e-32 | 6.2262e-32 | 3.704e-32 | 3.8974e-32 | 1.2001e-31 | 2.2665e-32 | 1.5044e-32
5 | 5.1 | 5.1.3 | Standard Deviation | 0.044071 | 0.016127 | 0.0034678 | 0.044794 | 0.015536 | 0.043836 | 0.088862 | 3.6291e-15 | 0.18523 | 0 | 0.11519 | 0 | 0.17419 | 1.4516e-14 | 0.083512 | 0 | 0.14058 | 0 | 0.0002733 | 0.011625 | 0.00033422 | 0.021081 | 0.00024077 | 0.014515 | 0.025013 | 0.028715 | 0.0089522 | 0.046607 | 5.7874e-18 | 0.00016901 | 0.019106 | 0.016127 | 9.9333e-05 | 7.0629e-05 | 8.2512e-05 | 0 | 0 | 0 | 6.2459e-07 | 3.8507e-07 | 7.7462e-07 | 6.6193e-05 | 0.0003704 | 5.4217e-05 | 0.00042322 | 5.2248e-05 | 0.00042692 | 0.00016478 | 0.00010309 | 0.00026594 | 6.6542e-05 | 0.00021762 | 0.00012498 | 0.0040459 | 0.0019448 | 0.0065302 | 0.0012488 | 0.0053435 | 0.0023531 | 2.0786e-07 | 2.1821e-07 | 2.1464e-07 | 2.3253e-07 | 2.6438e-07 | 2.1736e-07 | 1.8573e-07 | 8.5194e-32 | 6.4914e-32 | 4.3312e-32 | 3.95e-32 | 1.2688e-31 | 2.8977e-32 | 1.342e-32
5 | 5.2 | 5.2.1 | Standard Deviation | 0.25246 | 0.25989 | 0.31003 | 0.03315 | 0.065607 | 0.069774 | 0.076805 | 3.6291e-15 | 0.11049 | 0 | 0.077217 | 0 | 0.13487 | 1.4516e-14 | 0.082251 | 0 | 0.16014 | 0 | 0.00073455 | 0.090534 | 0.00061886 | 0.023265 | 0.00027585 | 0.014118 | 0.13984 | 0.11927 | 0.010967 | 0.028211 | 3.0072e-17 | 0.0028815 | 0.064884 | 0.25989 | 0.00035124 | 0.00063838 | 0.00033454 | 0.0044545 | 0.0030273 | 0.0030833 | 0.10827 | 0.072752 | 0.074671 | 8.8931e-05 | 0.0059684 | 8.2539e-05 | 0.0012625 | 0.00023359 | 0.0017183 | 0.00045886 | 0.00034345 | 0.00033528 | 0.00049287 | 0.0033978 | 0.0038872 | 0.011231 | 0.0067791 | 0.008212 | 0.0095166 | 0.083017 | 0.072376 | 0.00010298 | 7.2654e-06 | 2.6978e-06 | 2.2896e-06 | 0.1139 | 2.3419e-06 | 3.7695e-06 | 0.00072534 | 1.5491e-28 | 1.3785e-29 | 5.0909e-30 | 3.8616e-21 | 1.1516e-29 | 9.3115e-29
5 | 5.2 | 5.2.2 | Standard Deviation | 0.14775 | 0.13311 | 0.10429 | 0.043101 | 0.044569 | 0.075109 | 0.11551 | 4.1906e-15 | 0.1913 | 0 | 0.090718 | 0 | 0.14206 | 8.3811e-15 | 0.094312 | 0 | 0.18604 | 0 | 0.00025673 | 0.056574 | 0.00031152 | 0.026832 | 0.00030794 | 0.013378 | 0.086028 | 0.073204 | 0.0091039 | 0.048284 | 3.2223e-17 | 0.0011382 | 0.011316 | 0.13311 | 0.00015751 | 0.0004377 | 0.00022009 | 0.0012597 | 0.0014427 | 0.0019393 | 0.030655 | 0.034513 | 0.047356 | 4.9142e-05 | 0.0068655 | 5.2635e-05 | 0.00077585 | 8.509e-05 | 0.00074562 | 0.00047206 | 0.00039095 | 0.00040326 | 0.00040565 | 0.0010684 | 0.0012249 | 0.011543 | 0.0083342 | 0.0098666 | 0.0077267 | 0.026107 | 0.023008 | 0.00011034 | 9.9653e-07 | 9.7639e-07 | 5.3443e-07 | 6.9526e-07 | 1.6187e-07 | 4.1161e-07 | 0.0007772 | 2.5151e-29 | 7.2677e-30 | 2.1267e-30 | 3.9302e-30 | 9.8612e-31 | 1.0547e-29
5 | 5.2 | 5.2.3 | Standard Deviation | 0.082842 | 0.094043 | 0.082653 | 0.037503 | 0.031752 | 0.036176 | 0.084053 | 3.6291e-15 | 0.15797 | 0 | 0.10468 | 0 | 0.18042 | 1.4516e-14 | 0.088437 | 0 | 0.13968 | 0 | 0.00020928 | 0.04982 | 0.00019606 | 0.025736 | 0.0002711 | 0.014166 | 0.04819 | 0.068321 | 0.014837 | 0.040085 | 2.315e-17 | 0.0012012 | 0.013721 | 0.094043 | 0.00024817 | 0.00034867 | 0.00020108 | 0.00090686 | 0.0010892 | 0.0012561 | 0.021879 | 0.026112 | 0.030441 | 5.4424e-05 | 0.0022368 | 6.6382e-05 | 0.00069202 | 9.4147e-05 | 0.00068193 | 0.0004792 | 0.00050862 | 0.00044648 | 0.00049324 | 0.0014974 | 0.0017208 | 0.011732 | 0.0096689 | 0.010914 | 0.0093049 | 0.036592 | 0.032127 | 7.065e-05 | 2.5695e-07 | 4.1093e-07 | 2.2784e-07 | 3.2075e-07 | 3.6052e-07 | 6.801e-07 | 0.00049761 | 6.6397e-30 | 3.4128e-30 | 9.7163e-31 | 2.0107e-30 | 2.2356e-30 | 1.7347e-29
5 | 5.3 | 5.3.1 | Standard Deviation | 0.39427 | 0.38649 | 0.46438 | 0.021254 | 0.75988 | 0.76808 | 0.086236 | 4.0575e-15 | 0.13415 | 0 | 0.077691 | 0 | 0.1298 | 1.4516e-14 | 0.061637 | 0 | 0.1302 | 0 | 0.00083159 | 0.010532 | 0.0007744 | 0.013804 | 0.00018152 | 0.010604 | 0.23782 | 0.1741 | 0.0089926 | 0.035482 | 7.6779e-17 | 0.0032269 | 0.010613 | 0.38649 | 0.0016672 | 0.0003583 | 0.00042788 | 0.0055124 | 0.0059751 | 0.0050316 | 0.13126 | 0.14486 | 0.12181 | 0.00017019 | 0.00045113 | 7.7998e-05 | 0.0011462 | 0.0054399 | 0.0022779 | 0.00097955 | 0.00069327 | 0.00039902 | 0.0003652 | 0.0083177 | 0.010514 | 0.023542 | 0.01322 | 0.0096705 | 0.0082379 | 0.20309 | 0.19054 | 0.00037062 | 0.00010606 | 0.00012961 | 0.00027541 | 2.4512e-05 | 2.1103e-05 | 1.4843e-05 | 0.0026004 | 0.00074252 | 0.00091475 | 0.0018573 | 1.3053e-27 | 9.4401e-28 | 7.8317e-28
5 | 5.3 | 5.3.2 | Standard Deviation | 0.13189 | 0.13359 | 0.16596 | 0.024653 | 0.25204 | 0.2484 | 0.098377 | 3.6291e-15 | 0.15701 | 0 | 0.081988 | 0 | 0.13158 | 1.4516e-14 | 0.073542 | 0 | 0.15331 | 0 | 0.00053036 | 0.01046 | 0.00037994 | 0.013656 | 0.00021727 | 0.011575 | 0.12058 | 0.048003 | 0.0081454 | 0.040192 | 9.5449e-17 | 0.0019509 | 0.0071569 | 0.13359 | 0.0022051 | 0.00022977 | 0.0002415 | 0.002521 | 0.0018145 | 0.0029034 | 0.058257 | 0.043844 | 0.07029 | 4.3154e-05 | 0.00072317 | 5.666e-05 | 0.0010797 | 0.0042081 | 0.00090668 | 0.00044956 | 0.00035647 | 0.00085162 | 0.00038371 | 0.0035851 | 0.004376 | 0.010944 | 0.0074421 | 0.020722 | 0.0082225 | 0.085702 | 0.07996 | 0.00018365 | 7.0358e-05 | 0.00010899 | 7.3483e-05 | 9.5793e-06 | 1.808e-06 | 2.8253e-06 | 0.0012886 | 0.0004926 | 0.00076922 | 0.00049557 | 3.7322e-28 | 1.01e-28 | 1.6252e-28
5 | 5.3 | 5.3.3 | Standard Deviation | 0.20867 | 0.19225 | 0.22519 | 0.030641 | 0.076516 | 0.070366 | 0.082396 | 3.8493e-15 | 0.13675 | 0 | 0.079848 | 0 | 0.14099 | 0 | 0.085975 | 0 | 0.15193 | 0 | 0.00057888 | 0.008939 | 0.00051065 | 0.010287 | 0.00026055 | 0.0094467 | 0.08397 | 0.13547 | 0.0060569 | 0.035207 | 1.1341e-16 | 0.0021981 | 0.0060526 | 0.19225 | 0.0029616 | 0.00050381 | 0.0002076 | 0.0017341 | 0.002533 | 0.002062 | 0.038467 | 0.060967 | 0.049873 | 4.2349e-05 | 0.00042487 | 6.1038e-05 | 0.0030618 | 0.0005355 | 0.0016005 | 0.00052008 | 0.00036966 | 0.00047033 | 0.00062748 | 0.0061512 | 0.0078924 | 0.012617 | 0.0069924 | 0.011425 | 0.017078 | 0.14872 | 0.14258 | 9.3339e-05 | 5.684e-05 | 7.0876e-05 | 6.5984e-05 | 2.0412e-05 | 1.9429e-06 | 2.4735e-06 | 0.00065498 | 0.00039795 | 0.00050022 | 0.000445 | 7.6464e-28 | 1.0949e-28 | 1.36e-28
5 | 5.4 | 5.4.1 | Standard Deviation | 1.3703 | 1.3504 | 0.2496 | 0.025826 | 1.5742 | 1.5934 | 0.069762 | 3.8493e-15 | 0.1418 | 0 | 0.093092 | 0 | 0.152 | 1.4516e-14 | 0.072878 | 0 | 0.11545 | 0 | 0.0023358 | 0.019631 | 0.0024351 | 0.010668 | 0.00018294 | 0.013318 | 0.63947 | 0.74457 | 0.0075678 | 0.040323 | 1.3696e-16 | 0.0091253 | 0.021492 | 1.3504 | 0.0018871 | 0.0002647 | 0.00022652 | 0.0038722 | 0.0042652 | 0.0039859 | 0.091668 | 0.10301 | 0.096291 | 0.00014631 | 0.0015403 | 0.00013853 | 0.002452 | 0.00019348 | 0.0021245 | 0.00064606 | 0.00098323 | 0.00052273 | 0.00050683 | 0.0036896 | 0.0065539 | 0.015667 | 0.021893 | 0.012802 | 0.0069723 | 0.088529 | 0.12033 | 0.00034472 | 0.00021682 | 0.00021058 | 0.00038193 | 0.00046327 | 0.00021232 | 0.00043228 | 0.0024104 | 0.0015127 | 0.0014811 | 0.0025663 | 0.0031819 | 0.0013858 | 0.0028962
5 | 5.4 | 5.4.2 | Standard Deviation | 0.44502 | 0.46112 | 0.20389 | 0.032145 | 0.63991 | 0.62104 | 0.13235 | 4.0575e-15 | 0.23622 | 0 | 0.11894 | 0 | 0.17228 | 1.1853e-14 | 0.11211 | 0 | 0.21733 | 0 | 0.0017401 | 0.021541 | 0.0015765 | 0.018528 | 0.00030487 | 0.013323 | 0.25504 | 0.22162 | 0.0053375 | 0.059156 | 1.1341e-16 | 0.0067346 | 0.01607 | 0.46112 | 0.0031127 | 0.0001995 | 0.00018399 | 0.0024515 | 0.0021793 | 0.0020636 | 0.060464 | 0.052567 | 0.049783 | 0.00020317 | 0.0010429 | 0.00017323 | 0.0007589 | 0.0017334 | 0.0015948 | 0.00067687 | 0.00056138 | 0.00062943 | 0.0008089 | 0.003525 | 0.0042821 | 0.015883 | 0.013225 | 0.015651 | 0.017144 | 0.084746 | 0.07348 | 0.000223 | 7.4922e-05 | 7.3949e-05 | 8.6231e-05 | 0.00010497 | 0.00010265 | 0.00045971 | 0.0015592 | 0.00052271 | 0.00052012 | 0.00057945 | 0.00072096 | 0.00067001 | 0.00308
5 | 5.4 | 5.4.3 | Standard Deviation | 0.27329 | 0.27425 | 0.035225 | 0.034363 | 0.2967 | 0.29386 | 0.12065 | 3.8493e-15 | 0.21631 | 0 | 0.11275 | 5.9263e-15 | 0.16574 | 1.1853e-14 | 0.095883 | 0 | 0.18747 | 0 | 0.0013225 | 0.01927 | 0.0011188 | 0.013838 | 0.00028796 | 0.014282 | 0.18085 | 0.13182 | 0.0071563 | 0.058015 | 1.268e-16 | 0.0048877 | 0.021624 | 0.27425 | 0.0018564 | 8.6475e-05 | 0.00012738 | 0.00097488 | 0.00076551 | 0.0015011 | 0.022528 | 0.018471 | 0.03622 | 7.2534e-05 | 0.00023668 | 9.7253e-05 | 0.00068549 | 0.00013716 | 0.00057459 | 0.00045033 | 0.00048329 | 0.0006041 | 0.00049092 | 0.0021278 | 0.0023945 | 0.0108 | 0.0087154 | 0.014699 | 0.010531 | 0.050971 | 0.044968 | 0.0001389 | 8.3874e-05 | 8.7416e-05 | 0.00013404 | 9.3467e-05 | 9.3928e-05 | 0.00038104 | 0.00097117 | 0.00058515 | 0.00061483 | 0.0009007 | 0.00064197 | 0.00061305 | 0.0025528
6 | 6.1 | 6.1.1 | Standard Deviation | 0.049056 | 0.022104 | 0.052171 | 0.04729 | 0.051825 | 0.074813 | 0.10591 | 3.8493e-15 | 0.20258 | 0 | 0.1246 | 0 | 0.19649 | 9.3704e-15 | 0.089374 | 0 | 0.15673 | 0 | 0.00038894 | 0.018845 | 0.00057192 | 0.039303 | 0.00043674 | 0.13928 | 0.063348 | 0.023148 | 0.02844 | 0.067511 | 0 | 0.00043833 | 0.0090364 | 0.022104 | 9.3825e-05 | 8.2189e-05 | 0.0001391 | 0 | 0 | 0 | 3.9669e-07 | 3.1683e-07 | 8.036e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0072924 | 0.0027751 | 0 | 0 | 0 | 0 | 0.17939 | 0.052171 | 2.1876e-07 | 2.3765e-07 | 2.5094e-07 | 3.1276e-07 | 3.4867e-07 | 3.2835e-07 | 2.7424e-07 | 7.264e-32 | 5.2351e-32 | 3.489e-32 | 1.7163e-32 | 1.7029e-31 | 3.9172e-32 | 2.795e-32
6 | 6.1 | 6.1.2 | Standard Deviation | 0.055376 | 0.021786 | 0.003205 | 0.050485 | 0.021824 | 0.056431 | 0.10849 | 3.6291e-15 | 0.1925 | 0 | 0.1224 | 0 | 0.20264 | 1.4516e-14 | 0.11309 | 0 | 0.20132 | 0 | 0.00037118 | 0.018681 | 0.00049397 | 0.0299 | 0.00057237 | 0.18701 | 0.064493 | 0.013945 | 0.016505 | 0.0855 | 0 | 0.00049524 | 0.01105 | 0.021786 | 8.2221e-05 | 6.6513e-05 | 0.00020616 | 0 | 0 | 0 | 3.3205e-07 | 3.4021e-07 | 6.5786e-07 | 4.5204e-05 | 0.00054917 | 6.7468e-05 | 0.00053486 | 6.801e-05 | 0.00053266 | 0.00014953 | 9.1179e-05 | 0.00017568 | 6.8983e-05 | 0.0001689 | 0.0001452 | 0.003671 | 0.0017216 | 0.0043139 | 0.0012942 | 0.0041479 | 0.0027314 | 1.9194e-07 | 2.0187e-07 | 2.5027e-07 | 1.7914e-07 | 3.1545e-07 | 2.0718e-07 | 3.1017e-07 | 6.1804e-32 | 5.9568e-32 | 4.4461e-32 | 2.9727e-32 | 1.7838e-31 | 3.439e-32 | 2.7114e-32
6 | 6.1 | 6.1.3 | Standard Deviation | 0.050949 | 0.020365 | 0.0033324 | 0.043415 | 0.021741 | 0.051605 | 0.10544 | 4.1906e-15 | 0.17132 | 0 | 0.091505 | 0 | 0.15676 | 8.3811e-15 | 0.097534 | 0 | 0.18187 | 0 | 0.00034856 | 0.017271 | 0.00044887 | 0.01976 | 0.00048512 | 0.15026 | 0.060753 | 0.01485 | 0.01578 | 0.073673 | 0 | 0.00037629 | 0.009269 | 0.020365 | 8.99e-05 | 4.8191e-05 | 0.00010566 | 0 | 0 | 0 | 4.4547e-07 | 3.3325e-07 | 7.9411e-07 | 5.3912e-05 | 0.00044231 | 5.4729e-05 | 0.00051768 | 6.0934e-05 | 0.00045591 | 0.00018002 | 9.3438e-05 | 0.00017668 | 0.00010665 | 0.00017458 | 9.6694e-05 | 0.0044197 | 0.0017628 | 0.004338 | 0.0019988 | 0.004287 | 0.0018222 | 2.4003e-07 | 2.1811e-07 | 2.084e-07 | 1.9948e-07 | 2.2458e-07 | 2.2922e-07 | 2.8175e-07 | 8.7242e-32 | 6.6151e-32 | 3.975e-32 | 3.5278e-32 | 1.2477e-31 | 3.8792e-32 | 1.9457e-32
6 | 6.2 | 6.2.1 | Standard Deviation | 0.48455 | 0.49333 | 0.33233 | 0.031607 | 0.20569 | 0.20511 | 0.086305 | 4.3826e-15 | 0.15846 | 0 | 0.10193 | 0 | 0.18423 | 5.9263e-15 | 0.099879 | 0 | 0.15621 | 0 | 0.00099534 | 0.24218 | 0.0015607 | 0.62371 | 0.002025 | 0.48991 | 0.74127 | 0.60926 | 0.34732 | 0.075691 | 0 | 0.008994 | 0.26522 | 0.49333 | 0.0016273 | 0.00091461 | 0.00094493 | 0.0045962 | 0.0037906 | 0.0048908 | 0.10998 | 0.093215 | 0.12006 | 0.0011371 | 0.00030076 | 0.001137 | 0.0030364 | 0.0011212 | 0.00020301 | 0.00082038 | 0.00044801 | 0.00039863 | 0.00036468 | 0.00047834 | 0.00033027 | 0.019831 | 0.0083985 | 0.009871 | 0.0069346 | 0.011418 | 0.0061868 | 0.0014782 | 1.7701e-05 | 4.1226e-06 | 1.8972e-06 | 2.8501e-06 | 3.778e-06 | 1.7588e-05 | 0.010406 | 2.455e-28 | 9.7082e-30 | 1.9232e-30 | 2.2929e-30 | 7.7761e-30 | 3.5652e-28
6 | 6.2 | 6.2.2 | Standard Deviation | 0.21153 | 0.21631 | 0.22198 | 0.047236 | 0.014772 | 0.046487 | 0.09646 | 3.6291e-15 | 0.18848 | 0 | 0.11566 | 0 | 0.19867 | 9.8277e-15 | 0.099433 | 0 | 0.15073 | 0 | 0.00037612 | 0.021116 | 0.00027493 | 0.24588 | 0.00073897 | 0.038151 | 0.1051 | 0.040625 | 0.14851 | 0.07564 | 0 | 0.001548 | 0.018955 | 0.21631 | 0.0011543 | 0.00029988 | 0.00040113 | 0.0042668 | 0.00049247 | 0.0049972 | 0.10214 | 0.011954 | 0.12145 | 3.8459e-05 | 0.00014169 | 5.0212e-05 | 0.00081612 | 5.192e-05 | 0.00026682 | 0.00062215 | 0.00035597 | 0.00042115 | 0.00030837 | 0.00029367 | 0.0003488 | 0.015217 | 0.0066606 | 0.010305 | 0.0057276 | 0.0071854 | 0.0065634 | 0.00017388 | 7.3443e-07 | 1.0098e-06 | 2.3963e-07 | 5.5711e-07 | 9.8765e-07 | 9.3637e-07 | 0.0012242 | 1.6112e-29 | 5.6656e-30 | 6.4061e-31 | 1.9197e-30 | 2.6348e-30 | 2.4647e-29
6 | 6.2 | 6.2.3 | Standard Deviation | 0.17734 | 0.16546 | 0.1548 | 0.031213 | 0.022363 | 0.040228 | 0.068139 | 4.5665e-15 | 0.11893 | 0 | 0.071944 | 0 | 0.13735 | 1.1853e-14 | 0.077151 | 0 | 0.11958 | 0 | 0.00029338 | 0.013348 | 0.00026692 | 0.17378 | 0.00032671 | 0.022926 | 0.060727 | 0.036865 | 0.10799 | 0.05789 | 0 | 0.00066775 | 0.012182 | 0.16546 | 0.0003778 | 0.00024933 | 0.00026214 | 0.0024088 | 0.0016176 | 0.0027203 | 0.058622 | 0.039403 | 0.066124 | 3.6471e-05 | 0.0001742 | 4.4792e-05 | 0.0031565 | 3.6796e-05 | 0.00020931 | 0.00072183 | 0.00030627 | 0.00048342 | 0.00071341 | 0.00033722 | 0.000438 | 0.017659 | 0.0057536 | 0.011828 | 0.013028 | 0.0082458 | 0.0081992 | 0.00024725 | 9.2062e-07 | 6.6422e-07 | 4.2305e-07 | 5.3726e-07 | 4.7215e-07 | 1.0974e-06 | 0.0017408 | 2.0329e-29 | 3.9169e-30 | 9.1261e-31 | 1.9338e-30 | 7.8472e-31 | 2.8776e-29
6 | 6.3 | 6.3.1 | Standard Deviation | 0.43885 | 0.42164 | 0.30552 | 0.047499 | 0.58108 | 0.59815 | 0.12218 | 3.6291e-15 | 0.20584 | 0 | 0.11812 | 0 | 0.2078 | 1.4516e-14 | 0.12174 | 0 | 0.21344 | 0 | 0.00059386 | 0.0088419 | 0.00094913 | 0.017584 | 0.0013847 | 0.012819 | 0.14217 | 0.06016 | 0.29862 | 0.093618 | 0 | 0.0024655 | 0.017916 | 0.42164 | 0.039356 | 0.00023054 | 0.00031351 | 0.0077332 | 0.0051601 | 0.0041547 | 0.2302 | 0.12517 | 0.10063 | 5.1468e-05 | 0.0013433 | 4.8719e-05 | 0.0044911 | 0.00067937 | 0.0016795 | 0.00042538 | 0.00065623 | 0.00097149 | 0.00067758 | 0.0041474 | 0.0052216 | 0.010358 | 0.014663 | 0.023625 | 0.020365 | 0.099893 | 0.093549 | 0.00021383 | 0.00011131 | 0.00012132 | 0.00027237 | 2.8575e-05 | 2.584e-05 | 2.2738e-05 | 0.0015005 | 0.0007793 | 0.00085623 | 0.0018369 | 9.6973e-28 | 1.1047e-27 | 1.1034e-27
6 | 6.3 | 6.3.2 | Standard Deviation | 0.45316 | 0.42864 | 0.50286 | 0.036865 | 0.15707 | 0.16059 | 0.091709 | 4.1906e-15 | 0.14818 | 0 | 0.075846 | 0 | 0.13185 | 1.4516e-14 | 0.085701 | 0 | 0.15867 | 0 | 0.00064663 | 0.0062324 | 0.00055304 | 0.014953 | 0.0010439 | 0.004872 | 0.13511 | 0.06776 | 0.28948 | 0.065637 | 0 | 0.0020031 | 0.016579 | 0.42864 | 0.042463 | 0.00013138 | 0.00027421 | 0.010657 | 0.0017487 | 0.0023171 | 0.30866 | 0.042391 | 0.056011 | 8.9264e-05 | 0.00053765 | 7.8428e-05 | 0.00064725 | 0.00093962 | 0.0020806 | 0.00040044 | 0.00037339 | 0.00047647 | 0.00043184 | 0.0082533 | 0.010121 | 0.0097091 | 0.0072691 | 0.011559 | 0.0078871 | 0.19969 | 0.18252 | 0.0001036 | 0.00011499 | 9.5701e-05 | 9.7779e-05 | 8.2233e-06 | 3.3427e-06 | 2.4282e-06 | 0.00072698 | 0.00080508 | 0.00067543 | 0.00065945 | 2.6997e-28 | 1.7248e-28 | 1.3254e-28
6 | 6.3 | 6.3.3 | Standard Deviation | 0.056465 | 0.040656 | 0.049805 | 0.048096 | 0.039651 | 0.067674 | 0.12071 | 3.6291e-15 | 0.2104 | 0 | 0.12061 | 0 | 0.21322 | 1.4516e-14 | 0.12679 | 0 | 0.21415 | 0 | 0.00019747 | 0.0079854 | 0.00081314 | 0.021507 | 0.00079559 | 0.01022 | 0.096102 | 0.052181 | 0.033251 | 0.097413 | 0 | 0.0012277 | 0.016644 | 0.040656 | 0.0068524 | 0.00017821 | 0.00012295 | 0.00036796 | 0.00063533 | 0.0015601 | 0.016482 | 0.015552 | 0.037778 | 6.4138e-05 | 0.00078338 | 4.8045e-05 | 0.00014353 | 0.00050629 | 0.0007649 | 0.00038318 | 0.00038725 | 0.00053327 | 0.00044954 | 0.0010031 | 0.0016874 | 0.0093582 | 0.0081165 | 0.012969 | 0.0081302 | 0.024944 | 0.030468 | 6.7699e-05 | 5.4211e-05 | 6.219e-05 | 5.0903e-05 | 3.2837e-06 | 2.0076e-06 | 1.4026e-06 | 0.00047508 | 0.00037954 | 0.00043892 | 0.00034331 | 8.0445e-29 | 1.0158e-28 | 7.3592e-29
6 | 6.4 | 6.4.1 | Standard Deviation | 1.8379 | 1.8203 | 0.43065 | 0.035724 | 2.173 | 2.1883 | 0.12491 | 3.6291e-15 | 0.25337 | 0 | 0.16787 | 0 | 0.2929 | 1.4516e-14 | 0.146 | 0 | 0.21314 | 0 | 0.0023789 | 0.010121 | 0.0032963 | 0.011785 | 0.0056736 | 0.0094506 | 0.28007 | 0.29783 | 1.2755 | 0.11376 | 0 | 0.010681 | 0.03474 | 1.8203 | 0.0023675 | 0.00055613 | 0.00048516 | 0.0058981 | 0.0068879 | 0.00607 | 0.1391 | 0.16622 | 0.1465 | 0.0004371 | 0.0064748 | 0.00026681 | 0.0086199 | 0.0014989 | 0.0037621 | 0.0032526 | 0.0024626 | 0.0013312 | 0.0016858 | 0.0097317 | 0.012104 | 0.077176 | 0.070742 | 0.032783 | 0.062503 | 0.23061 | 0.22217 | 0.0016563 | 0.00020473 | 0.00025754 | 0.0002645 | 0.00071159 | 0.00068551 | 0.00064778 | 0.011582 | 0.0014283 | 0.0018113 | 0.0017773 | 0.0048872 | 0.0044747 | 0.0043401
6 | 6.4 | 6.4.2 | Standard Deviation | 0.47717 | 0.43239 | 0.20973 | 0.089318 | 0.45594 | 0.48473 | 0.10708 | 4.1906e-15 | 0.17084 | 0 | 0.087871 | 0 | 0.15014 | 1.0265e-14 | 0.094151 | 0 | 0.18011 | 0 | 0.00067105 | 0.010228 | 0.0010032 | 0.012449 | 0.0015996 | 0.0072079 | 0.14751 | 0.11299 | 0.3249 | 0.079796 | 0 | 0.0029931 | 0.011368 | 0.43239 | 0.0022168 | 0.00037185 | 0.00044782 | 0.0032468 | 0.0028724 | 0.0030307 | 0.0758 | 0.069145 | 0.07289 | 0.00034844 | 0.0017107 | 0.00033039 | 0.00067663 | 0.00035077 | 0.0017528 | 0.0011408 | 0.00069449 | 0.00050012 | 0.00050122 | 0.0030328 | 0.0038739 | 0.026698 | 0.01819 | 0.012777 | 0.011037 | 0.072537 | 0.068216 | 0.00052789 | 0.00018959 | 8.6004e-05 | 0.00018742 | 0.00023404 | 0.0011663 | 0.00025824 | 0.0036913 | 0.0013227 | 0.00060487 | 0.0012593 | 0.0016075 | 0.0076129 | 0.00173
6 | 6.4 | 6.4.3 | Standard Deviation | 0.17732 | 0.12694 | 0.13202 | 0.076266 | 0.13023 | 0.15495 | 0.1017 | 4.3826e-15 | 0.17646 | 0 | 0.10255 | 0 | 0.16517 | 5.9263e-15 | 0.085897 | 0 | 0.16219 | 0 | 0.00028388 | 0.013835 | 0.00076224 | 0.017998 | 0.00099658 | 0.0079113 | 0.099135 | 0.12497 | 0.12268 | 0.068362 | 0 | 0.0017754 | 0.010148 | 0.12694 | 0.0027808 | 0.00024421 | 0.00023274 | 0.0014245 | 0.00273 | 0.0019599 | 0.031151 | 0.065824 | 0.047188 | 0.00017105 | 0.0011782 | 0.00014408 | 0.00058925 | 0.00037483 | 0.0011005 | 0.00051494 | 0.00044494 | 0.00048758 | 0.00030776 | 0.0042944 | 0.0049424 | 0.012088 | 0.0079805 | 0.012068 | 0.0063442 | 0.10249 | 0.088579 | 0.00024162 | 8.9701e-05 | 5.6072e-05 | 7.654e-05 | 0.00042541 | 0.00028863 | 8.8881e-05 | 0.0016894 | 0.0006258 | 0.00039436 | 0.00051428 | 0.0029218 | 0.0018838 | 0.00059543
5 | 5.1 | All | Standard Deviation | 0.049273 | 0.024263 | 0.0055387 | 0.027206 | 0.019617 | 0.043858 | 0.090744 | 0 | 0.18488 | 0 | 0.11644 | 0 | 0.18832 | 0.0039512 | 0.098356 | 0 | 0.15894 | 0.016458 | 0.00032309 | 0.019686 | 0.00033042 | 0.04658 | 0.00023692 | 0.041131 | 0.010608 | 0.020586 | 0.033703 | 0.046826 | 0.00035806 | 2.6291e-05 | 0.032222 | 0.024263 | 0.00029432 | 8.0057e-05 | 0.00026077 | 0 | 0 | 0 | 2.7621e-07 | 1.5818e-07 | 8.5857e-07 | 0.00040036 | 0.0054602 | 0.00040443 | 0.0064577 | 0.00040207 | 0.0060211 | 0.00086597 | 0.00022444 | 0.00012402 | 8.7372e-05 | 0.0008089 | 8.5598e-05 | 0.021284 | 0.0042697 | 0.0030542 | 0.0016786 | 0.019883 | 0.0015863 | 1.0313e-07 | 1.221e-07 | 1.4972e-07 | 6.8975e-08 | 1.5737e-07 | 1.7591e-07 | 2.7628e-07 | 4.2689e-32 | 4.0961e-32 | 2.4903e-32 | 7.5585e-33 | 7.5431e-32 | 1.872e-32 | 2.3053e-32
5 | 5.2 | All | Standard Deviation | 0.90326 | 0.95843 | 0.91964 | 0.055163 | 0.083546 | 0.073586 | 0.021557 | 0 | 0.05026 | 0 | 0.11164 | 0 | 0.29098 | 0.037634 | 0.13855 | 0 | 0.081826 | 0.010071 | 0.0018639 | 0.1159 | 0.0017881 | 0.07991 | 0.00028174 | 0.002768 | 0.4412 | 0.48081 | 0.019205 | 0.017507 | 0.001073 | 0.0092301 | 0.049244 | 0.95843 | 0.000828 | 0.0025394 | 0.001189 | 0.013988 | 0.012009 | 0.013432 | 0.34025 | 0.28836 | 0.32516 | 5.955e-05 | 0.0070293 | 7.6576e-05 | 0.0056785 | 8.6532e-05 | 0.0051339 | 0.00044649 | 4.5926e-05 | 0.00045501 | 0.00057794 | 0.0020703 | 0.0023439 | 0.01091 | 0.0029959 | 0.011156 | 0.012122 | 0.050626 | 0.044609 | 0.00034004 | 9.9583e-06 | 7.5195e-06 | 5.0766e-06 | 0.033204 | 2.9236e-06 | 1.2704e-06 | 0.0023951 | 2.3277e-28 | 4.9432e-29 | 1.5797e-29 | 1.1047e-21 | 1.6039e-29 | 3.1392e-29
5 | 5.3 | All | Standard Deviation | 0.59627 | 0.6025 | 1.2202 | 0.05491 | 1.7572 | 1.7294 | 0.14809 | 0 | 0.26282 | 0 | 0.11962 | 0 | 0.154 | 0.021655 | 0.06214 | 0 | 0.16578 | 0.0078332 | 0.0012299 | 0.039233 | 0.00098407 | 0.033495 | 0.00036627 | 0.03162 | 0.40967 | 0.17218 | 0.022838 | 0.062774 | 0.0016003 | 0.0041157 | 0.040535 | 0.6025 | 0.013829 | 0.0019036 | 0.0015001 | 0.018923 | 0.020064 | 0.019472 | 0.44135 | 0.48554 | 0.47153 | 7.0406e-05 | 0.0021667 | 2.7006e-05 | 0.007411 | 0.00095663 | 0.0047462 | 0.0036252 | 0.00028418 | 0.0014261 | 0.0015721 | 0.0056677 | 0.0085908 | 0.087978 | 0.0051494 | 0.034729 | 0.044439 | 0.1375 | 0.16731 | 0.0010724 | 0.00029236 | 0.00026783 | 0.00052503 | 5.1007e-05 | 2.8893e-05 | 9.7861e-06 | 0.0075248 | 0.0020469 | 0.0018902 | 0.0035408 | 2.3117e-27 | 1.4369e-27 | 5.3204e-28
5 | 5.4 | All | Standard Deviation | 2.5004 | 2.6371 | 1.0105 | 0.22376 | 3.6031 | 3.4481 | 0.15667 | 0 | 0.1509 | 0 | 0.05701 | 0 | 0.097071 | 0.025912 | 0.12872 | 0 | 0.31781 | 0.015422 | 0.0043537 | 0.05625 | 0.0043015 | 0.022351 | 0.00039074 | 0.026443 | 1.4865 | 1.0263 | 0.025512 | 0.067532 | 0.00019714 | 0.015945 | 0.072862 | 2.6371 | 0.013066 | 0.0013055 | 0.001415 | 0.012059 | 0.015732 | 0.015132 | 0.27355 | 0.37949 | 0.36479 | 0.0010568 | 0.0054974 | 0.00088213 | 0.0014979 | 0.0035167 | 0.0094774 | 0.0026947 | 0.0014321 | 0.0016711 | 0.0019626 | 0.0022823 | 0.0014322 | 0.06148 | 0.047252 | 0.042856 | 0.036959 | 0.043885 | 0.011356 | 0.0010628 | 0.00026218 | 0.00031346 | 0.00061527 | 0.00056897 | 0.00030004 | 0.00084834 | 0.0074312 | 0.0018292 | 0.0022047 | 0.0041344 | 0.0039078 | 0.0019583 | 0.0056837
6 | 6.1 | All | Standard Deviation | 0.069555 | 0.024568 | 0.13989 | 0.045949 | 0.11532 | 0.073208 | 0.045347 | 0 | 0.02715 | 0 | 0.031942 | 0 | 0.06382 | 0.011409 | 0.021624 | 0 | 0.076261 | 0.0050111 | 8.2848e-05 | 0.018096 | 0.00032238 | 0.017551 | 0.0002332 | 0.097939 | 0.014638 | 0.016823 | 0.052718 | 0.016326 | 0.0090107 | 0.00047034 | 0.014004 | 0.024568 | 0.00040605 | 0.00023808 | 0.00065294 | 0 | 0 | 0 | 2.7327e-08 | 5.2469e-08 | 4.5799e-07 | 0.027849 | 0.024943 | 0.027702 | 0.025511 | 0.027897 | 0.020265 | 0.0063829 | 0.00087469 | 0.0042044 | 0.0017428 | 0.0057939 | 0.0065727 | 0.15602 | 0.016375 | 0.1042 | 0.032937 | 0.14369 | 0.12332 | 1.8624e-07 | 1.0648e-07 | 1.648e-07 | 3.815e-07 | 1.6918e-07 | 1.73e-07 | 7.5947e-08 | 6.5066e-32 | 2.7978e-32 | 2.6158e-32 | 3.3731e-32 | 8.8917e-32 | 2.0019e-32 | 6.8141e-33
6 | 6.2 | All | Standard Deviation | 1.5531 | 1.4856 | 1.5679 | 0.073376 | 0.091004 | 0.070658 | 0.10573 | 0 | 0.20333 | 0 | 0.17918 | 0 | 0.39744 | 0.015502 | 0.21803 | 0 | 0.27044 | 0.010838 | 0.0020022 | 0.1336 | 0.0044816 | 0.24399 | 0.0024822 | 0.63923 | 0.79917 | 0.24487 | 0.98151 | 0.15777 | 0.022156 | 0.0081185 | 0.1269 | 1.4856 | 0.0014412 | 0.0015322 | 0.0016833 | 0.022117 | 0.012867 | 0.029204 | 0.53486 | 0.31199 | 0.71041 | 0.00035497 | 0.0010786 | 0.00040037 | 0.0029717 | 0.0005558 | 0.0014845 | 0.0012237 | 0.00035875 | 0.00017781 | 0.00023052 | 0.00069139 | 0.00029461 | 0.029821 | 0.0063993 | 0.0043441 | 0.0032998 | 0.016717 | 0.0059628 | 0.0019352 | 1.8702e-05 | 9.0111e-06 | 3.9357e-06 | 7.2964e-06 | 2.2859e-06 | 1.1883e-05 | 0.013624 | 3.2419e-28 | 3.545e-29 | 6.8877e-30 | 1.5071e-29 | 5.0043e-30 | 2.6517e-28
6 | 6.3 | All | Standard Deviation | 0.2369 | 0.26203 | 1.3054 | 0.046333 | 1.391 | 1.4137 | 0.13216 | 0 | 0.24531 | 0 | 0.13411 | 0 | 0.19153 | 0.017192 | 0.09635 | 0 | 0.19328 | 0.012125 | 0.00023336 | 0.0069179 | 0.00089339 | 0.032354 | 0.0011363 | 0.01614 | 0.057052 | 0.10714 | 0.18882 | 0.077023 | 0.018709 | 0.0019702 | 0.039089 | 0.26203 | 0.019949 | 0.00044494 | 0.0012517 | 0.020779 | 0.013506 | 0.016215 | 0.52425 | 0.32782 | 0.39261 | 6.1313e-05 | 0.0023396 | 0.00012574 | 0.0023998 | 0.00071449 | 0.0061739 | 0.0016122 | 0.00044359 | 0.0002398 | 0.00016427 | 0.00389 | 0.0043844 | 0.039066 | 0.013409 | 0.0060612 | 0.0024225 | 0.095419 | 0.06721 | 0.00021918 | 0.0001583 | 0.00013537 | 0.00052462 | 2.9044e-05 | 1.5964e-05 | 8.0201e-06 | 0.0015381 | 0.0011083 | 0.00095542 | 0.0035381 | 9.1645e-28 | 7.2824e-28 | 3.9878e-28
6 | 6.4 | All | Standard Deviation | 1.8226 | 2.3925 | 1.3348 | 0.57092 | 3.7051 | 3.1402 | 0.14045 | 0 | 0.28147 | 0 | 0.19158 | 0 | 0.35524 | 0.017572 | 0.19121 | 0 | 0.27091 | 0.024568 | 0.002392 | 0.0034608 | 0.0025438 | 0.022099 | 0.0048765 | 0.020979 | 0.44049 | 0.18296 | 1.2094 | 0.18902 | 0.021036 | 0.009424 | 0.044491 | 2.3925 | 0.0057428 | 0.0021333 | 0.0024432 | 0.022011 | 0.023717 | 0.02213 | 0.52251 | 0.57191 | 0.53312 | 0.001788 | 0.010102 | 0.0013896 | 0.0074099 | 0.002618 | 0.0091766 | 0.008449 | 0.0037043 | 0.0016766 | 0.0021837 | 0.010582 | 0.014143 | 0.19816 | 0.10815 | 0.045015 | 0.068536 | 0.24706 | 0.29172 | 0.0010064 | 0.00039581 | 0.0001921 | 0.00031754 | 0.00054372 | 0.0012786 | 0.0015275 | 0.0070369 | 0.0027614 | 0.0013511 | 0.0021336 | 0.0037343 | 0.0083456 | 0.010234
5 | 5.1 | 5.1.1 | Mean | 72.4425 | 19.8664 | 0.50161 | 52.5761 | 19.3647 | 71.9409 | 283.3295 | -30 | 491.1839 | 0 | 283.5011 | -150 | 490.4497 | -120.0873 | 282.9052 | 90 | 490.1795 | 120.0363 | 0.25067 | -105.2962 | 0.35839 | 146.4269 | 0.36549 | 6.0017 | 16.9269 | 44.8829 | 10.6327 | 123.5335 | -0.046649 | 0.4731 | -70.1745 | 19.8664 | 0.24804 | 0.17061 | 0.22085 | 0 | 0 | 0 | 3.3434e-06 | 7.1674e-07 | -9.5267e-06 | 24.5506 | 18.8667 | 24.5509 | 18.7695 | 24.5506 | 18.8468 | 0.059521 | 0.0068882 | 0.049227 | 0.0072146 | 0.059267 | 0.012535 | 1.4613 | 0.12996 | 1.2086 | 0.13541 | 1.455 | 0.23624 | 2.0062e-06 | 1.5505e-06 | 8.8871e-07 | 6.0767e-07 | 2.1899e-06 | 7.2833e-07 | 6.5679e-07 | 4.6588e-31 | 2.8772e-31 | 1.0813e-31 | 5.8956e-32 | 5.5166e-31 | 7.4893e-32 | 6.2465e-32
5 | 5.1 | 5.1.2 | Mean | 72.3865 | 19.8279 | 0.49725 | 52.5586 | 19.3307 | 71.8893 | 283.4722 | -30 | 491.5256 | 0 | 283.7178 | -150 | 490.7641 | -120.084 | 283.0321 | 90 | 490.368 | 120.019 | 0.25118 | -105.3096 | 0.35896 | 146.3619 | 0.3658 | 5.9362 | 16.9469 | 44.8624 | 10.5772 | 123.62 | -0.045982 | 0.47306 | -70.2266 | 19.8279 | 0.24849 | 0.17077 | 0.22116 | 0 | 0 | 0 | 3.0675e-06 | 7.3227e-07 | -8.3971e-06 | 24.5512 | 18.8591 | 24.5515 | 18.7605 | 24.5511 | 18.8384 | 0.060948 | 0.0065476 | 0.049161 | 0.0071779 | 0.060448 | 0.012693 | 1.4964 | 0.12348 | 1.207 | 0.13466 | 1.4841 | 0.23911 | 1.8e-06 | 1.3144e-06 | 6.2187e-07 | 5.0962e-07 | 1.9962e-06 | 3.7747e-07 | 2.12e-07 | 3.8054e-31 | 2.0882e-31 | 6.1965e-32 | 5.0495e-32 | 4.6448e-31 | 3.8596e-32 | 2.8452e-32
5 | 5.1 | 5.1.3 | Mean | 72.3442 | 19.8215 | 0.49061 | 52.5227 | 19.3309 | 71.8536 | 283.4979 | -30 | 491.4771 | 0 | 283.6834 | -150 | 490.7865 | -120.0919 | 283.0989 | 90 | 490.4954 | 120.0034 | 0.25126 | -105.3349 | 0.35897 | 146.3365 | 0.36596 | 5.9258 | 16.9308 | 44.8417 | 10.5718 | 123.6078 | -0.04609 | 0.47311 | -70.2335 | 19.8215 | 0.24858 | 0.1707 | 0.22137 | 0 | 0 | 0 | 2.791e-06 | 4.5086e-07 | -7.8419e-06 | 24.5514 | 18.8561 | 24.5516 | 18.7569 | 24.5513 | 18.8351 | 0.061083 | 0.0064648 | 0.049401 | 0.0070483 | 0.060815 | 0.012557 | 1.4997 | 0.1219 | 1.2129 | 0.1322 | 1.4931 | 0.23651 | 1.9063e-06 | 1.3784e-06 | 8.7298e-07 | 6.4267e-07 | 2.3079e-06 | 5.3046e-07 | 1.5048e-07 | 4.2547e-31 | 2.2917e-31 | 1.0123e-31 | 6.5574e-32 | 6.147e-31 | 4.8792e-32 | 1.8501e-32
5 | 5.2 | 5.2.1 | Mean | 293.2615 | 238.7229 | 196.9966 | 54.5386 | 41.7264 | 96.265 | 282.9324 | -30 | 491.3372 | 0 | 284.0056 | -150 | 491.2053 | -120.2911 | 282.856 | 90 | 489.3803 | 119.8906 | 0.43036 | -27.0579 | 0.76198 | 169.5541 | 0.36565 | 5.776 | 118.208 | 164.4521 | 10.6015 | 122.7382 | -0.2259 | 2.0761 | -20.6957 | 238.7229 | 24.4003 | 24.2876 | 24.3213 | 1.2656 | 1.2907 | 1.2469 | 30.8805 | 31.3481 | 30.3263 | 24.4626 | 18.5773 | 24.4605 | 18.6636 | 24.4545 | 18.7685 | 0.34557 | 0.3105 | 0.34721 | 0.32653 | 0.33337 | 0.36628 | 8.4535 | 5.7682 | 8.493 | 6.0941 | 8.1524 | 6.8746 | 24.3356 | 9.7858e-05 | 2.2928e-05 | 9.8152e-06 | 0.057484 | -2.2647e-05 | -0.00011299 | 85.7047 | 1.0697e-27 | 5.9202e-29 | 1.1273e-29 | 1.9134e-21 | 5.7584e-29 | 1.42e-27
5 | 5.2 | 5.2.2 | Mean | 294.2238 | 239.7438 | 198.0957 | 54.48 | 41.6481 | 96.1281 | 282.9727 | -30 | 491.3299 | 0 | 283.8911 | -150 | 490.8925 | -120.2176 | 282.7196 | 90 | 489.3341 | 119.9051 | 0.43233 | -26.9338 | 0.76373 | 169.6945 | 0.36521 | 5.7813 | 118.6778 | 164.9573 | 10.5887 | 122.7313 | -0.22772 | 2.0861 | -20.7743 | 239.7438 | 24.3994 | 24.2841 | 24.3199 | 1.2843 | 1.3057 | 1.2626 | 31.336 | 31.7071 | 30.7051 | 24.4625 | 18.5636 | 24.4604 | 18.6571 | 24.4545 | 18.7632 | 0.34578 | 0.31042 | 0.34631 | 0.32677 | 0.32927 | 0.3617 | 8.4587 | 5.7625 | 8.4709 | 6.0966 | 8.052 | 6.7867 | 24.3351 | 0.00011356 | 3.354e-05 | 1.7926e-05 | -2.5514e-05 | -2.7449e-05 | -0.00011543 | 85.7017 | 1.433e-27 | 1.251e-28 | 3.575e-29 | 7.2399e-29 | 8.3729e-29 | 1.4805e-27
5 | 5.2 | 5.2.3 | Mean | 295.0668 | 240.6384 | 198.8233 | 54.4284 | 41.8151 | 96.2435 | 282.9393 | -30 | 491.2467 | 0 | 283.7823 | -150 | 490.6239 | -120.2684 | 282.5789 | 90 | 489.2212 | 119.9099 | 0.43408 | -26.8263 | 0.76555 | 169.6905 | 0.36513 | 5.7773 | 119.0897 | 165.4133 | 10.5637 | 122.705 | -0.2278 | 2.0945 | -20.7864 | 240.6384 | 24.3987 | 24.2827 | 24.3189 | 1.2929 | 1.3145 | 1.2736 | 31.5461 | 31.9185 | 30.9735 | 24.4625 | 18.5729 | 24.4604 | 18.6522 | 24.4543 | 18.7582 | 0.34643 | 0.3105 | 0.34665 | 0.32567 | 0.33179 | 0.36485 | 8.4744 | 5.7669 | 8.4793 | 6.0745 | 8.1138 | 6.8439 | 24.3349 | 0.00011632 | 3.7463e-05 | 1.916e-05 | -2.8301e-05 | -2.7938e-05 | -0.00011483 | 85.7 | 1.5034e-27 | 1.5598e-28 | 4.0811e-29 | 8.9019e-29 | 8.6753e-29 | 1.465e-27
5 | 5.3 | 5.3.1 | Mean | 693.7042 | 628.2147 | 550.8536 | 65.4895 | 77.361 | 142.8505 | 280.693 | -30 | 486.2867 | 0 | 280.7281 | -150 | 486.0719 | -120.0226 | 280.5689 | 90 | 486.0421 | 119.9961 | 1.228 | -8.0983 | 1.5766 | 178.8576 | 0.35737 | 6.3366 | 304.9746 | 377.8126 | 10.917 | 119.9111 | -0.55941 | 5.3823 | -13.8098 | 628.2147 | 24.1801 | 24.3162 | 24.3134 | 1.2257 | 1.2118 | 1.2385 | 29.6367 | 29.4664 | 30.112 | 24.3036 | 18.3497 | 24.3224 | 18.1881 | 24.2769 | 18.4809 | 1.9402 | 2.2872 | 1.8232 | 2.2273 | 1.8093 | 2.2541 | 47.1538 | 41.9702 | 44.344 | 40.5095 | 43.9243 | 41.6581 | 24.2422 | 24.2588 | 24.2778 | 24.2778 | -0.00024953 | -0.00020296 | -0.00023941 | 85.0486 | 84.9189 | 85.6703 | 81.863 | 6.9832e-27 | 4.6245e-27 | 6.3921e-27
5 | 5.3 | 5.3.2 | Mean | 692.5631 | 627.0983 | 552.2561 | 65.4648 | 74.8422 | 140.307 | 280.4805 | -30 | 485.9981 | 0 | 280.6909 | -150 | 486.1521 | -119.9992 | 280.5694 | 90 | 485.8198 | 120.0022 | 1.2266 | -8.1146 | 1.5752 | 178.9144 | 0.35736 | 6.3335 | 304.2004 | 377.4706 | 10.8922 | 119.8273 | -0.56201 | 5.3773 | -13.8508 | 627.0983 | 24.171 | 24.3147 | 24.3116 | 1.2503 | 1.2339 | 1.2619 | 30.2198 | 30.0014 | 30.6787 | 24.3035 | 18.3529 | 24.3223 | 18.1882 | 24.2776 | 18.4767 | 1.9442 | 2.2874 | 1.8223 | 2.2262 | 1.7985 | 2.2387 | 47.2515 | 41.9799 | 44.3224 | 40.4904 | 43.6634 | 41.3646 | 24.2435 | 24.2593 | 24.2781 | 24.2787 | -0.00017388 | -0.00025166 | -0.00025887 | 85.0575 | 84.9223 | 85.6727 | 81.8687 | 3.3692e-27 | 7.0376e-27 | 7.4466e-27
5 | 5.3 | 5.3.3 | Mean | 692.8335 | 627.2637 | 553.2845 | 65.5698 | 73.9791 | 139.549 | 280.7654 | -30 | 486.5229 | 0 | 280.9142 | -150 | 486.3695 | -120.0425 | 280.6768 | 90 | 486.1441 | 119.9866 | 1.2255 | -8.1729 | 1.5747 | 178.8552 | 0.358 | 6.2804 | 304.3551 | 377.607 | 10.8714 | 119.9502 | -0.56232 | 5.3741 | -13.8908 | 627.2637 | 24.1529 | 24.3124 | 24.3104 | 1.2629 | 1.2519 | 1.2772 | 30.5021 | 30.4358 | 31.0481 | 24.3034 | 18.3538 | 24.3223 | 18.1753 | 24.2757 | 18.4714 | 1.9474 | 2.2868 | 1.8204 | 2.2242 | 1.8009 | 2.2398 | 47.3294 | 41.972 | 44.276 | 40.4248 | 43.7185 | 41.3722 | 24.2444 | 24.2593 | 24.2783 | 24.2788 | -0.00015243 | -0.00025424 | -0.00024731 | 85.0635 | 84.9225 | 85.674 | 81.8695 | 2.6788e-27 | 7.1827e-27 | 6.7962e-27
5 | 5.4 | 5.4.1 | Mean | 1084.0215 | 995.9209 | 883.003 | 88.1006 | 112.9179 | 201.0185 | 280.7072 | -30 | 486.4028 | 0 | 280.8457 | -150 | 486.2716 | -120.013 | 280.6315 | 90 | 486.0643 | 120.0035 | 2.0278 | -5.657 | 2.3791 | 179.8535 | 0.35759 | 6.2994 | 496.5224 | 576.6345 | 10.8646 | 118.2651 | -0.83406 | 8.5472 | -10.6903 | 995.9209 | 24.0268 | 24.2253 | 24.2243 | 1.217 | 1.22 | 1.2221 | 29.24 | 29.5538 | 29.6046 | 24.1604 | 18.1104 | 24.1794 | 17.9302 | 24.1329 | 18.19 | 3.4561 | 4.0747 | 3.2283 | 3.9632 | 3.1795 | 3.9384 | 83.4998 | 73.795 | 78.0571 | 71.062 | 76.7312 | 71.6403 | 24.1584 | 24.1741 | 24.1951 | 24.19 | 24.176 | 24.1819 | 24.1862 | 84.4614 | 84.3273 | 85.0877 | 81.2716 | 83.0225 | 78.9158 | 81.0209
5 | 5.4 | 5.4.2 | Mean | 1079.5172 | 991.3395 | 884.3088 | 88.1777 | 107.0307 | 195.2084 | 280.4009 | -30 | 486.1099 | 0 | 280.7757 | -150 | 486.0845 | -120.0634 | 280.3862 | 90 | 485.4673 | 119.9766 | 2.0203 | -5.7434 | 2.3714 | 179.8886 | 0.35735 | 6.25 | 493.7647 | 574.907 | 10.8455 | 118.158 | -0.83367 | 8.5187 | -10.8093 | 991.3395 | 24.0098 | 24.2238 | 24.2229 | 1.2326 | 1.2404 | 1.2407 | 29.5943 | 30.0469 | 30.0527 | 24.1591 | 18.1197 | 24.1783 | 17.9309 | 24.1276 | 18.1786 | 3.4599 | 4.0763 | 3.2252 | 3.9597 | 3.1829 | 3.9402 | 83.5883 | 73.8609 | 77.9787 | 71.0007 | 76.7967 | 71.6282 | 24.1573 | 24.1744 | 24.1952 | 24.191 | 24.177 | 24.1824 | 24.187 | 84.4538 | 84.3293 | 85.0885 | 81.2786 | 83.0298 | 78.9186 | 81.0265
5 | 5.4 | 5.4.3 | Mean | 1079.8879 | 991.367 | 884.9919 | 88.5209 | 106.3752 | 194.8961 | 280.6111 | -30 | 486.1931 | 0 | 280.7327 | -150 | 486.1332 | -120.0487 | 280.5765 | 90 | 485.9548 | 119.977 | 2.0202 | -5.7627 | 2.372 | 179.8471 | 0.35811 | 6.2911 | 494.1814 | 574.8105 | 10.896 | 118.1404 | -0.83392 | 8.5206 | -10.8227 | 991.367 | 24.0012 | 24.2227 | 24.2215 | 1.2407 | 1.2509 | 1.2521 | 29.7781 | 30.3001 | 30.3273 | 24.1583 | 18.1202 | 24.1776 | 17.928 | 24.1263 | 18.1712 | 3.4613 | 4.0776 | 3.2256 | 3.96 | 3.1838 | 3.9413 | 83.618 | 73.8866 | 77.988 | 70.9956 | 76.8145 | 71.6176 | 24.1563 | 24.1739 | 24.1946 | 24.1899 | 24.1769 | 24.1818 | 24.1853 | 84.4465 | 84.3257 | 85.0844 | 81.2713 | 83.0286 | 78.9149 | 81.0152
6 | 6.1 | 6.1.1 | Mean | 71.9857 | 19.4338 | 0.72133 | 52.5519 | 18.7124 | 71.2643 | 283.0144 | -30 | 490.7645 | 0 | 283.3904 | -150 | 490.3598 | -120.1154 | 282.7805 | 90 | 489.7395 | 119.9817 | 0.37477 | -81.3546 | 0.30144 | 108.9444 | 0.12977 | 54.8607 | 65.542 | -17.2243 | 23.668 | 213.5308 | 89.8053 | 0.67491 | 7.5554 | 19.4338 | 0.17925 | 0.15165 | 0.33294 | 0 | 0 | 0 | -5.5135e-06 | -5.4221e-06 | 0.00013803 | 24.6 | 18.9 | 24.6 | 18.8 | 24.6 | 18.8 | 0.024797 | 0.0047813 | 0.035334 | 0.0098002 | 0.051654 | 0.023755 | 0.61 | 0.090366 | 0.86922 | 0.18424 | 1.2707 | 0.44659 | 1.3927e-06 | 1.0601e-06 | 5.9748e-07 | 8.64e-08 | 2.3029e-06 | 4.0762e-07 | 4.2928e-07 | 2.3691e-31 | 1.4453e-31 | 5.9905e-32 | 2.4891e-32 | 6.1639e-31 | 4.049e-32 | 4.3111e-32
6 | 6.1 | 6.1.2 | Mean | 71.8807 | 19.3904 | 0.47701 | 52.4903 | 18.9134 | 71.4037 | 283.042 | -30 | 490.8156 | 0 | 283.3866 | -150 | 490.2919 | -120.1276 | 282.7393 | 90 | 489.7265 | 119.9722 | 0.37486 | -81.3708 | 0.30177 | 108.9239 | 0.12974 | 54.7292 | 65.5297 | -17.2523 | 23.6033 | 213.4998 | 89.7906 | 0.6745 | 7.529 | 19.3904 | 0.17877 | 0.152 | 0.33202 | 0 | 0 | 0 | -5.5233e-06 | -5.4297e-06 | 0.00013766 | 24.5517 | 18.8585 | 24.5519 | 18.7578 | 24.5516 | 18.8367 | 0.035815 | 0.006277 | 0.027751 | 0.0067793 | 0.041497 | 0.012281 | 0.87932 | 0.11838 | 0.68134 | 0.12716 | 1.0188 | 0.23134 | 1.4499e-06 | 1.2454e-06 | 7.6902e-07 | 6.9668e-07 | 2.5739e-06 | 6.4017e-07 | 3.1927e-07 | 2.5089e-31 | 1.9246e-31 | 8.6632e-32 | 7.2706e-32 | 7.6498e-31 | 6.3309e-32 | 3.2976e-32
6 | 6.1 | 6.1.3 | Mean | 71.8542 | 19.3921 | 0.48112 | 52.4621 | 18.911 | 71.373 | 282.9534 | -30 | 490.7742 | 0 | 283.4437 | -150 | 490.4195 | -120.1382 | 282.7483 | 90 | 489.6014 | 119.9798 | 0.37493 | -81.3907 | 0.30209 | 108.9589 | 0.12935 | 54.6692 | 65.5129 | -17.2222 | 23.5635 | 213.5063 | 89.789 | 0.67397 | 7.534 | 19.3921 | 0.17844 | 0.15211 | 0.33168 | 0 | 0 | 0 | -5.4718e-06 | -5.5166e-06 | 0.00013712 | 24.5519 | 18.8553 | 24.5521 | 18.7541 | 24.5518 | 18.8332 | 0.03589 | 0.0063148 | 0.028396 | 0.0067838 | 0.041744 | 0.012462 | 0.88115 | 0.11907 | 0.69718 | 0.12722 | 1.0249 | 0.2347 | 1.7401e-06 | 1.2437e-06 | 9.2699e-07 | 7.8813e-07 | 2.6138e-06 | 7.4577e-07 | 2.8357e-07 | 3.5594e-31 | 1.935e-31 | 1.1222e-31 | 9.0014e-32 | 7.7529e-31 | 8.0391e-32 | 3.0153e-32
6 | 6.2 | 6.2.1 | Mean | 288.906 | 235.0779 | 194.433 | 53.8281 | 40.6449 | 94.473 | 282.7851 | -30 | 490.4032 | 0 | 283.1024 | -150 | 489.6871 | -120.1 | 282.3712 | 90 | 489.1694 | 120.0062 | 0.63916 | -79.3401 | 0.083054 | 144.7834 | 0.61975 | 94.8165 | 116.8797 | 3.643 | 168.3832 | 212.2656 | 89.6859 | 1.4527 | 49.3613 | 235.0779 | 24.2633 | 24.3968 | 24.3991 | 1.2343 | 1.2299 | 1.2227 | 29.949 | 30.0047 | 29.8323 | 24.4647 | 18.7255 | 24.4643 | 18.5052 | 24.4574 | 18.7525 | 0.35467 | 0.31622 | 0.35319 | 0.32595 | 0.35281 | 0.37745 | 8.6769 | 5.9214 | 8.6407 | 6.0318 | 8.6287 | 7.0782 | 24.3229 | 6.6433e-05 | 1.034e-05 | 4.3714e-06 | -3.2548e-06 | -1.0204e-05 | -9.731e-05 | 85.6156 | 5.238e-28 | 1.3704e-29 | 2.5191e-30 | 2.0586e-30 | 1.3109e-29 | 1.0852e-27
6 | 6.2 | 6.2.2 | Mean | 290.5292 | 236.678 | 196.1883 | 53.8512 | 40.4897 | 94.3408 | 282.7964 | -30 | 490.4085 | 0 | 283.1101 | -150 | 489.7228 | -120.1132 | 282.4 | 90 | 489.2111 | 120.0055 | 0.64174 | -79.1443 | 0.082545 | 144.8695 | 0.62459 | 95.1443 | 117.8228 | 3.2413 | 169.465 | 212.2813 | 89.6685 | 1.4663 | 49.1657 | 236.678 | 24.2612 | 24.3953 | 24.3972 | 1.2574 | 1.2435 | 1.2574 | 30.5053 | 30.3364 | 30.6776 | 24.4653 | 18.7244 | 24.465 | 18.5068 | 24.4582 | 18.7512 | 0.35297 | 0.31679 | 0.35335 | 0.32581 | 0.35196 | 0.37759 | 8.6354 | 5.9317 | 8.6447 | 6.0297 | 8.6084 | 7.0804 | 24.3246 | 9.8439e-05 | 2.5129e-05 | 1.2091e-05 | -1.5523e-05 | -1.1797e-05 | -0.00011824 | 85.6273 | 1.0768e-27 | 7.0282e-29 | 1.6263e-29 | 2.6823e-29 | 1.5581e-29 | 1.5535e-27
6 | 6.2 | 6.2.3 | Mean | 292.0112 | 238.046 | 197.561 | 53.9651 | 40.4851 | 94.4502 | 282.9736 | -30 | 490.758 | 0 | 283.4165 | -150 | 490.3926 | -120.1309 | 282.7624 | 90 | 489.6573 | 119.9871 | 0.6431 | -79.0847 | 0.07505 | 144.4105 | 0.62314 | 96.0506 | 118.4689 | 3.1996 | 170.3427 | 212.5464 | 89.6419 | 1.4672 | 49.4035 | 238.046 | 24.2605 | 24.3937 | 24.3957 | 1.2786 | 1.2556 | 1.2807 | 31.0184 | 30.6282 | 31.244 | 24.4653 | 18.7234 | 24.465 | 18.5109 | 24.4584 | 18.7496 | 0.3523 | 0.31689 | 0.35299 | 0.3255 | 0.35144 | 0.37703 | 8.6191 | 5.9332 | 8.636 | 6.0253 | 8.5956 | 7.0691 | 24.3268 | 9.9199e-05 | 2.6654e-05 | 9.5649e-06 | -1.6233e-05 | -7.2894e-06 | -0.00011753 | 85.6428 | 1.0935e-27 | 7.8999e-29 | 1.0198e-29 | 2.9321e-29 | 5.946e-30 | 1.5349e-27
6 | 6.3 | 6.3.1 | Mean | 680.8696 | 619.3418 | 551.6878 | 61.5277 | 67.6541 | 129.1818 | 280.7402 | -30 | 486.456 | 0 | 280.8457 | -150 | 486.2224 | -120.0287 | 280.6053 | 90 | 486.0724 | 120.0167 | 1.1098 | -79.0596 | 0.46652 | -160.0382 | 1.5726 | 98.8798 | 203.2398 | 47.2291 | 430.4007 | 209.1892 | 89.4782 | 3.251 | 65.0785 | 619.3418 | 24.07 | 24.3096 | 24.3121 | 1.2248 | 1.2407 | 1.2539 | 29.4822 | 30.1607 | 30.4861 | 24.3055 | 18.3561 | 24.323 | 18.1743 | 24.2659 | 18.4731 | 1.9423 | 2.2873 | 1.8233 | 2.2259 | 1.8024 | 2.251 | 47.2095 | 41.9854 | 44.3481 | 40.4541 | 43.7357 | 41.5831 | 24.245 | 24.2597 | 24.2784 | 24.2786 | -0.00016555 | -0.00020259 | -0.00022941 | 85.068 | 84.9255 | 85.6747 | 81.868 | 3.1324e-27 | 4.6318e-27 | 5.9028e-27
6 | 6.3 | 6.3.2 | Mean | 680.4089 | 618.8577 | 553.2295 | 61.5512 | 65.6281 | 127.1794 | 280.9519 | -30 | 486.7708 | 0 | 280.9763 | -150 | 486.4117 | -120.0479 | 280.7446 | 90 | 486.4027 | 119.9987 | 1.1095 | -79.0461 | 0.46492 | -160.0998 | 1.5706 | 98.8523 | 203.3519 | 47.0153 | 430.0417 | 209.2936 | 89.4554 | 3.2478 | 65.0194 | 618.8577 | 24.0814 | 24.3088 | 24.3107 | 1.2478 | 1.259 | 1.2729 | 30.0485 | 30.6054 | 30.9451 | 24.3055 | 18.3572 | 24.3228 | 18.1785 | 24.2655 | 18.4669 | 1.9437 | 2.2877 | 1.823 | 2.2256 | 1.8051 | 2.2543 | 47.2427 | 41.9953 | 44.3398 | 40.4586 | 43.8011 | 41.6304 | 24.2454 | 24.2596 | 24.2787 | 24.2795 | -0.00014754 | -0.00023207 | -0.00024535 | 85.0707 | 84.9249 | 85.6766 | 81.8741 | 2.426e-27 | 5.9852e-27 | 6.6892e-27
6 | 6.3 | 6.3.3 | Mean | 680.7353 | 619.2734 | 554.2834 | 61.4619 | 64.99 | 126.4518 | 280.7091 | -30 | 486.2875 | 0 | 280.7081 | -150 | 486.0287 | -120.0136 | 280.5596 | 90 | 486.0636 | 120.0218 | 1.11 | -79.05 | 0.46641 | -160.0518 | 1.5726 | 98.8808 | 203.2773 | 47.1352 | 430.3228 | 209.1433 | 89.4925 | 3.2514 | 65.0933 | 619.2734 | 24.1088 | 24.3089 | 24.3097 | 1.2663 | 1.267 | 1.2862 | 30.5295 | 30.8003 | 31.2673 | 24.3054 | 18.3527 | 24.3228 | 18.1786 | 24.2669 | 18.4608 | 1.9455 | 2.2868 | 1.8228 | 2.2256 | 1.81 | 2.2597 | 47.2873 | 41.9687 | 44.3364 | 40.4579 | 43.9236 | 41.7157 | 24.2454 | 24.2594 | 24.2786 | 24.2795 | -0.00010872 | -0.00022796 | -0.00023585 | 85.0707 | 84.9234 | 85.6758 | 81.8741 | 1.3145e-27 | 5.7745e-27 | 6.181e-27
6 | 6.4 | 6.4.1 | Mean | 1053.8244 | 977.9353 | 881.2904 | 75.8891 | 96.6449 | 172.534 | 280.6118 | -30 | 486.4043 | 0 | 280.8524 | -150 | 486.1266 | -120.0503 | 280.4514 | 90 | 485.743 | 119.9964 | 1.5543 | -80.804 | 0.90968 | -157.4812 | 2.4619 | 97.4493 | 274.5413 | 100.2194 | 679.0637 | 207.2897 | 89.2538 | 4.9673 | 71.0141 | 977.9353 | 24.0378 | 24.2247 | 24.2272 | 1.1901 | 1.1889 | 1.1961 | 28.6067 | 28.8017 | 28.9792 | 24.1615 | 18.1025 | 24.1811 | 17.9514 | 24.1203 | 18.2062 | 3.4399 | 4.0686 | 3.2282 | 3.9633 | 3.1895 | 3.9542 | 83.1139 | 73.6521 | 78.0606 | 71.1468 | 76.9315 | 71.9913 | 24.1587 | 24.1745 | 24.1934 | 24.1894 | 24.1755 | 24.1843 | 24.1868 | 84.4634 | 84.3302 | 85.0756 | 81.2677 | 83.0194 | 78.9313 | 81.025
6 | 6.4 | 6.4.2 | Mean | 1050.9293 | 974.0875 | 883.0239 | 76.8418 | 91.0636 | 167.9054 | 280.7268 | -30 | 486.5568 | 0 | 280.9982 | -150 | 486.5258 | -120.0607 | 280.7088 | 90 | 486.089 | 119.9519 | 1.55 | -80.8086 | 0.90462 | -157.451 | 2.4524 | 97.4116 | 273.9484 | 99.8985 | 677.0824 | 207.2904 | 89.2148 | 4.9492 | 70.9253 | 974.0875 | 24.0341 | 24.2218 | 24.2243 | 1.2183 | 1.2198 | 1.2232 | 29.2813 | 29.546 | 29.631 | 24.1593 | 18.1225 | 24.1794 | 17.9422 | 24.1242 | 18.1959 | 3.4534 | 4.0758 | 3.2263 | 3.9605 | 3.1715 | 3.9314 | 83.4308 | 73.8645 | 78.0109 | 71.0605 | 76.5108 | 71.5362 | 24.1592 | 24.1743 | 24.1937 | 24.1893 | 24.1766 | 24.1836 | 24.1846 | 84.4673 | 84.3287 | 85.0776 | 81.267 | 83.0267 | 78.9269 | 81.01
6 | 6.4 | 6.4.3 | Mean | 1050.4587 | 973.5481 | 883.9153 | 76.9106 | 89.6329 | 166.5435 | 280.4473 | -30 | 486.0113 | 0 | 280.6184 | -150 | 485.8173 | -120.0264 | 280.3352 | 90 | 485.5548 | 119.9922 | 1.5505 | -80.8108 | 0.90675 | -157.4382 | 2.4551 | 97.4145 | 273.6805 | 99.9067 | 676.8716 | 206.9627 | 89.2481 | 4.9538 | 70.9738 | 973.5481 | 24.0265 | 24.2205 | 24.2224 | 1.2334 | 1.2356 | 1.24 | 29.6352 | 29.926 | 30.0358 | 24.1579 | 18.1151 | 24.1783 | 17.9367 | 24.1253 | 18.1879 | 3.4555 | 4.0736 | 3.2248 | 3.959 | 3.1708 | 3.9283 | 83.4784 | 73.794 | 77.9708 | 71.0114 | 76.4967 | 71.4476 | 24.1573 | 24.1738 | 24.1938 | 24.1888 | 24.1763 | 24.1818 | 24.1839 | 84.4536 | 84.3249 | 85.0781 | 81.2637 | 83.0244 | 78.9151 | 81.0054
5 | 5.1 | All | Mean | 72.3911 | 19.8386 | 0.49649 | 52.5525 | 19.3421 | 71.8946 | 283.4332 | -30 | 491.3955 | 0 | 283.6341 | -150 | 490.6668 | -120.0877 | 283.0121 | 90 | 490.3477 | 120.0196 | 0.25104 | -105.3136 | 0.35877 | 146.3751 | 0.36575 | 5.9545 | 16.9349 | 44.8623 | 10.5939 | 123.5871 | -0.046241 | 0.47309 | -70.2115 | 19.8386 | 0.24837 | 0.17069 | 0.22113 | 0 | 0 | 0 | 3.0673e-06 | 6.3329e-07 | -8.5886e-06 | 24.5511 | 18.8606 | 24.5513 | 18.7623 | 24.551 | 18.8401 | 0.060517 | 0.0066335 | 0.049263 | 0.0071469 | 0.060177 | 0.012595 | 1.4858 | 0.12511 | 1.2095 | 0.13409 | 1.4774 | 0.23729 | 1.9042e-06 | 1.4144e-06 | 7.9452e-07 | 5.8666e-07 | 2.1647e-06 | 5.4542e-07 | 3.3976e-07 | 4.2396e-31 | 2.419e-31 | 9.0442e-32 | 5.8342e-32 | 5.4362e-31 | 5.4094e-32 | 3.6473e-32
5 | 5.2 | All | Mean | 294.184 | 239.7017 | 197.9718 | 54.4824 | 41.7299 | 96.2122 | 282.9481 | -30 | 491.3046 | 0 | 283.893 | -150 | 490.9072 | -120.2591 | 282.7181 | 90 | 489.3119 | 119.9019 | 0.43226 | -26.9393 | 0.76375 | 169.6464 | 0.36533 | 5.7782 | 118.6585 | 164.9409 | 10.5847 | 122.7249 | -0.22714 | 2.0856 | -20.7522 | 239.7017 | 24.3995 | 24.2848 | 24.32 | 1.2809 | 1.3036 | 1.261 | 31.2542 | 31.6579 | 30.6683 | 24.4626 | 18.5713 | 24.4605 | 18.6576 | 24.4544 | 18.7633 | 0.34592 | 0.31047 | 0.34673 | 0.32632 | 0.33148 | 0.36428 | 8.4622 | 5.7659 | 8.4811 | 6.0884 | 8.1061 | 6.8351 | 24.3352 | 0.00010925 | 3.1311e-05 | 1.5634e-05 | 0.019143 | -2.6011e-05 | -0.00011441 | 85.7022 | 1.3354e-27 | 1.1343e-28 | 2.9278e-29 | 6.3779e-22 | 7.6022e-29 | 1.4552e-27
5 | 5.3 | All | Mean | 693.0336 | 627.5255 | 552.1314 | 65.508 | 75.3941 | 140.9021 | 280.6463 | -30 | 486.2692 | 0 | 280.7777 | -150 | 486.1978 | -120.0215 | 280.6051 | 90 | 486.002 | 119.9949 | 1.2267 | -8.1286 | 1.5755 | 178.8757 | 0.35757 | 6.3168 | 304.51 | 377.63 | 10.8935 | 119.8962 | -0.56125 | 5.3779 | -13.8505 | 627.5255 | 24.168 | 24.3144 | 24.3118 | 1.2463 | 1.2325 | 1.2592 | 30.1196 | 29.9679 | 30.6129 | 24.3035 | 18.3522 | 24.3223 | 18.1838 | 24.2767 | 18.4763 | 1.944 | 2.2871 | 1.822 | 2.2259 | 1.8029 | 2.2442 | 47.2449 | 41.974 | 44.3141 | 40.4749 | 43.7687 | 41.465 | 24.2434 | 24.2591 | 24.2781 | 24.2784 | -0.00019194 | -0.00023629 | -0.00024853 | 85.0566 | 84.9212 | 85.6723 | 81.8671 | 4.3437e-27 | 6.2816e-27 | 6.8783e-27
5 | 5.4 | All | Mean | 1081.1422 | 992.8758 | 884.1012 | 88.2664 | 108.7746 | 197.041 | 280.5731 | -30 | 486.2353 | 0 | 280.7847 | -150 | 486.1631 | -120.0417 | 280.5314 | 90 | 485.8288 | 119.9857 | 2.0228 | -5.721 | 2.3742 | 179.8631 | 0.35769 | 6.2802 | 494.8228 | 575.4507 | 10.8687 | 118.1878 | -0.83388 | 8.5289 | -10.7741 | 992.8758 | 24.0126 | 24.224 | 24.2229 | 1.2301 | 1.2371 | 1.2383 | 29.5375 | 29.9669 | 29.9949 | 24.1593 | 18.1168 | 24.1784 | 17.9297 | 24.1289 | 18.18 | 3.4591 | 4.0762 | 3.2263 | 3.961 | 3.1821 | 3.94 | 83.5687 | 73.8475 | 78.0079 | 71.0194 | 76.7808 | 71.6287 | 24.1573 | 24.1741 | 24.195 | 24.1903 | 24.1766 | 24.182 | 24.1862 | 84.4539 | 84.3274 | 85.0869 | 81.2738 | 83.027 | 78.9165 | 81.0209
6 | 6.1 | All | Mean | 71.9068 | 19.4054 | 0.55982 | 52.5014 | 18.8456 | 71.347 | 283.0033 | -30 | 490.7848 | 0 | 283.4069 | -150 | 490.3571 | -120.1271 | 282.756 | 90 | 489.6891 | 119.9779 | 0.37485 | -81.372 | 0.30177 | 108.9424 | 0.12962 | 54.753 | 65.5282 | -17.2329 | 23.6116 | 213.5123 | 89.795 | 0.67446 | 7.5394 | 19.4054 | 0.17882 | 0.15192 | 0.33221 | 0 | 0 | 0 | -5.5029e-06 | -5.4561e-06 | 0.0001376 | 24.5678 | 18.8713 | 24.568 | 18.7706 | 24.5678 | 18.8233 | 0.032167 | 0.005791 | 0.030494 | 0.0077878 | 0.044965 | 0.016166 | 0.79016 | 0.10927 | 0.74925 | 0.14621 | 1.1048 | 0.30421 | 1.5276e-06 | 1.1831e-06 | 7.6449e-07 | 5.2374e-07 | 2.4969e-06 | 5.9785e-07 | 3.4404e-07 | 2.8125e-31 | 1.7683e-31 | 8.6251e-32 | 6.2537e-32 | 7.1889e-31 | 6.1397e-32 | 3.5414e-32
6 | 6.2 | All | Mean | 290.4821 | 236.6007 | 196.0608 | 53.8815 | 40.5399 | 94.4214 | 282.8517 | -30 | 490.5232 | 0 | 283.2097 | -150 | 489.9342 | -120.1147 | 282.5112 | 90 | 489.3459 | 119.9996 | 0.64133 | -79.1897 | 0.080216 | 144.6878 | 0.62249 | 95.3372 | 117.7238 | 3.3613 | 169.397 | 212.3645 | 89.6655 | 1.462 | 49.3101 | 236.6007 | 24.2617 | 24.3953 | 24.3973 | 1.2568 | 1.243 | 1.2536 | 30.4909 | 30.3231 | 30.5846 | 24.4651 | 18.7244 | 24.4648 | 18.5076 | 24.458 | 18.7511 | 0.35331 | 0.31663 | 0.35318 | 0.32575 | 0.35207 | 0.37736 | 8.6438 | 5.9288 | 8.6404 | 6.0289 | 8.6109 | 7.0759 | 24.3247 | 8.8024e-05 | 2.0708e-05 | 8.6757e-06 | -1.167e-05 | -9.7636e-06 | -0.00011102 | 85.6286 | 8.9802e-28 | 5.4328e-29 | 9.6599e-30 | 1.9401e-29 | 1.1545e-29 | 1.3912e-27
6 | 6.3 | All | Mean | 680.6712 | 619.1576 | 553.0669 | 61.5136 | 66.0907 | 127.6043 | 280.8004 | -30 | 486.5048 | 0 | 280.8434 | -150 | 486.2209 | -120.0301 | 280.6365 | 90 | 486.1795 | 120.0124 | 1.1098 | -79.0519 | 0.46595 | -160.0633 | 1.572 | 98.871 | 203.2896 | 47.1266 | 430.255 | 209.2087 | 89.4754 | 3.2501 | 65.0638 | 619.1576 | 24.0867 | 24.3091 | 24.3108 | 1.2463 | 1.2556 | 1.271 | 30.0201 | 30.5221 | 30.8995 | 24.3054 | 18.3554 | 24.3229 | 18.1771 | 24.2661 | 18.4669 | 1.9439 | 2.2872 | 1.823 | 2.2257 | 1.8058 | 2.255 | 47.2465 | 41.9832 | 44.3414 | 40.4569 | 43.8201 | 41.6431 | 24.2453 | 24.2596 | 24.2786 | 24.2792 | -0.0001406 | -0.00022087 | -0.00023687 | 85.0698 | 84.9246 | 85.6757 | 81.8721 | 2.291e-27 | 5.4638e-27 | 6.2577e-27
6 | 6.4 | All | Mean | 1051.7375 | 975.1903 | 882.7432 | 76.5472 | 92.4471 | 168.9943 | 280.5953 | -30 | 486.3241 | 0 | 280.823 | -150 | 486.1566 | -120.0458 | 280.4985 | 90 | 485.7956 | 119.9802 | 1.5516 | -80.8078 | 0.90702 | -157.4568 | 2.4565 | 97.4251 | 274.0567 | 100.0082 | 677.6726 | 207.1809 | 89.2389 | 4.9568 | 70.9711 | 975.1903 | 24.0328 | 24.2223 | 24.2247 | 1.2139 | 1.2148 | 1.2198 | 29.1744 | 29.4246 | 29.5487 | 24.1596 | 18.1134 | 24.1796 | 17.9434 | 24.1232 | 18.1966 | 3.4496 | 4.0727 | 3.2264 | 3.9609 | 3.1773 | 3.938 | 83.341 | 73.7702 | 78.0141 | 71.0729 | 76.6463 | 71.6583 | 24.1584 | 24.1742 | 24.1936 | 24.1892 | 24.1761 | 24.1833 | 24.1851 | 84.4614 | 84.3279 | 85.0771 | 81.2662 | 83.0235 | 78.9244 | 81.0135
5 | 5.1 | All | Covariance | [73 empty] | -1.8091e-09 | -2.2401e-06 | -6.0878e-06 | -4.2196e-11 | 3.4238e-07 | 2.3063e-08
5 | 5.2 | All | Covariance | [73 empty] | -7.6384e-06 | 0.00012358 | -0.0011377 | -2.0392e-05 | -1.5575e-08 | 3.4791e-08
5 | 5.3 | All | Covariance | [73 empty] | 5.4157e-05 | 7.6542e-05 | 0.00077512 | -0.00026845 | -2.3574e-07 | 3.2607e-08
5 | 5.4 | All | Covariance | [73 empty] | 0.00019237 | 8.9098e-05 | 0.0032446 | -0.0013184 | -2.8229e-06 | 1.2556e-06
6 | 6.1 | All | Covariance | [73 empty] | 1.8777e-07 | -3.0594e-06 | 1.5321e-05 | 8.1785e-10 | -0.00017775 | 0.00011616
6 | 6.2 | All | Covariance | [73 empty] | -1.1508e-05 | -3.4856e-05 | -0.0024994 | 0.00016775 | -4.0638e-07 | -4.1346e-09
6 | 6.3 | All | Covariance | [73 empty] | 1.2289e-05 | 7.6701e-06 | 7.4383e-05 | 0.00011703 | -9.8849e-08 | 3.0047e-08
6 | 6.4 | All | Covariance | [73 empty] | 3.0388e-05 | 5.9703e-05 | 0.0055929 | 0.0014843 | -1.4633e-05 | 2.3247e-06
Note on D98: Covariance for load V, I measurements only, placed in independent columns
Note on D99: Covariance for load V, I measurements only, placed in independent columns
Note on D100: Covariance for load V, I measurements only, placed in independent columns
Note on D101: Covariance for load V, I measurements only, placed in independent columns
Note on D102: Covariance for load V, I measurements only, placed in independent columns
Note on D103: Covariance for load V, I measurements only, placed in independent columns
Note on D104: Covariance for load V, I measurements only, placed in independent columns
Note on D105: Covariance for load V, I measurements only, placed in independent columns